## Table
4 to 20 mA Conversion Table
Basis: Linear signal scaling: mA = 4 + 16 × % ÷ 100. NAMUR NE 43 for signal limits and failure currents.
instrumentationblog.in/downloads/engineering-reference-tables/4-20-ma-conversion-table/
Signal conversion by percent of range
% | mA | 1 to 5 V | 0 to 10 V | 3 to 15 psi | 0.2 to 1.0 bar | 20 to 100 kPa
0 | 4 | 1 | 0 | 3 | 0.2 | 20
5 | 4.8 | 1.2 | 0.5 | 3.6 | 0.24 | 24
10 | 5.6 | 1.4 | 1 | 4.2 | 0.28 | 28
15 | 6.4 | 1.6 | 1.5 | 4.8 | 0.32 | 32
20 | 7.2 | 1.8 | 2 | 5.4 | 0.36 | 36
25 | 8 | 2 | 2.5 | 6 | 0.4 | 40
30 | 8.8 | 2.2 | 3 | 6.6 | 0.44 | 44
35 | 9.6 | 2.4 | 3.5 | 7.2 | 0.48 | 48
40 | 10.4 | 2.6 | 4 | 7.8 | 0.52 | 52
45 | 11.2 | 2.8 | 4.5 | 8.4 | 0.56 | 56
50 | 12 | 3 | 5 | 9 | 0.6 | 60
55 | 12.8 | 3.2 | 5.5 | 9.6 | 0.64 | 64
60 | 13.6 | 3.4 | 6 | 10.2 | 0.68 | 68
65 | 14.4 | 3.6 | 6.5 | 10.8 | 0.72 | 72
70 | 15.2 | 3.8 | 7 | 11.4 | 0.76 | 76
75 | 16 | 4 | 7.5 | 12 | 0.8 | 80
80 | 16.8 | 4.2 | 8 | 12.6 | 0.84 | 84
85 | 17.6 | 4.4 | 8.5 | 13.2 | 0.88 | 88
90 | 18.4 | 4.6 | 9 | 13.8 | 0.92 | 92
95 | 19.2 | 4.8 | 9.5 | 14.4 | 0.96 | 96
100 | 20 | 5 | 10 | 15 | 1 | 100
NAMUR NE 43 signal levels
Current | Meaning
3.8 to 20.5 mA | Normal measuring range including under and over range
Below 3.6 mA | Failure signal (low)
Above 21.0 mA | Failure signal (high)
3.6 to 3.8 and 20.5 to 21.0 mA | Not used for measurement; treat as suspect
Notes
• 1 to 5 V equals 4 to 20 mA across a 250 Ω resistor.
• Check the device burnout setting (high or low) before testing alarms.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: 4 to 20 mA Conversion Table
What this table is
4 to 20 mA conversion table for loop checks and calibration, with equivalent voltage and pneumatic signals for every 5 % of range.
Basis
Linear signal scaling: mA = 4 + 16 × % ÷ 100. NAMUR NE 43 for signal limits and failure currents.
How to use
1. Find the percent of range.
2. Read the expected mA or other signal.
3. Engineering value = LRV + % × (URV − LRV) ÷ 100.
Notes
1 to 5 V equals 4 to 20 mA across a 250 Ω resistor.
Check the device burnout setting (high or low) before testing alarms.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/4-20-ma-conversion-table/