## Table
BSP Thread Size Chart (ISO 228 and ISO 7)
Basis: ISO 228 1 (parallel, G) and ISO 7 1 (taper, R and Rc). Whitworth 55° form: thread depth h = 0.640327 × pitch. Taper threads share the gauge plane diameters.
instrumentationblog.in/downloads/engineering-reference-tables/bsp-thread-size-chart/
BSP sizes
Size | TPI | Pitch mm | Major dia mm | Minor dia mm | Pitch dia mm
1/16 | 28 | 0.907 | 7.723 | 6.561 | 7.142
1/8 | 28 | 0.907 | 9.728 | 8.566 | 9.147
1/4 | 19 | 1.337 | 13.157 | 11.445 | 12.301
3/8 | 19 | 1.337 | 16.662 | 14.95 | 15.806
1/2 | 14 | 1.814 | 20.955 | 18.632 | 19.793
5/8 | 14 | 1.814 | 22.911 | 20.588 | 21.749
3/4 | 14 | 1.814 | 26.441 | 24.118 | 25.279
1 | 11 | 2.309 | 33.249 | 30.292 | 31.77
1 1/4 | 11 | 2.309 | 41.91 | 38.953 | 40.431
1 1/2 | 11 | 2.309 | 47.803 | 44.846 | 46.324
2 | 11 | 2.309 | 59.614 | 56.657 | 58.135
2 1/2 | 11 | 2.309 | 75.184 | 72.227 | 73.705
3 | 11 | 2.309 | 87.884 | 84.927 | 86.405
4 | 11 | 2.309 | 113.03 | 110.073 | 111.551
Notes
• BSPP seals with a bonded washer or O ring, not on the thread.
• Diameters for taper threads apply at the gauge plane.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: BSP Thread Size Chart (ISO 228 and ISO 7)
What this table is
BSP thread chart for parallel (G, BSPP) and taper (R, Rc, BSPT) British Standard Pipe threads.
Basis
ISO 228 1 (parallel, G) and ISO 7 1 (taper, R and Rc). Whitworth 55° form: thread depth h = 0.640327 × pitch. Taper threads share the gauge plane diameters.
How to use
1. Measure the male thread outside diameter and count threads per inch.
2. G means parallel, R taper male, Rc taper female.
3. G 1/2 is the usual European gauge and transmitter connection.
Notes
BSPP seals with a bonded washer or O ring, not on the thread.
Diameters for taper threads apply at the gauge plane.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/bsp-thread-size-chart/