## Table
Carbon Steel Pipe Schedule Chart (ASME B36.10M)
Basis: ASME B36.10M Welded and Seamless Wrought Steel Pipe (metric values). Outside diameter is fixed for each NPS; the schedule sets the wall.
instrumentationblog.in/downloads/engineering-reference-tables/carbon-steel-pipe-schedule-chart/
Wall thickness in mm by schedule
NPS | DN | OD mm | Sch 10 | Sch 20 | Sch 30 | Sch 40 | STD | Sch 60 | Sch 80 | XS | Sch 100 | Sch 120 | Sch 140 | Sch 160 | XXS
1/8 | 6 | 10.3 | 1.24 |  | 1.45 | 1.73 | 1.73 |  | 2.41 | 2.41
1/4 | 8 | 13.7 | 1.65 |  | 1.85 | 2.24 | 2.24 |  | 3.02 | 3.02
3/8 | 10 | 17.1 | 1.65 |  | 1.85 | 2.31 | 2.31 |  | 3.2 | 3.2
1/2 | 15 | 21.3 | 2.11 |  | 2.41 | 2.77 | 2.77 |  | 3.73 | 3.73 |  |  |  | 4.78 | 7.47
3/4 | 20 | 26.7 | 2.11 |  | 2.41 | 2.87 | 2.87 |  | 3.91 | 3.91 |  |  |  | 5.56 | 7.82
1 | 25 | 33.4 | 2.77 |  | 2.9 | 3.38 | 3.38 |  | 4.55 | 4.55 |  |  |  | 6.35 | 9.09
1 1/4 | 32 | 42.2 | 2.77 |  | 2.97 | 3.56 | 3.56 |  | 4.85 | 4.85 |  |  |  | 6.35 | 9.7
1 1/2 | 40 | 48.3 | 2.77 |  | 3.18 | 3.68 | 3.68 |  | 5.08 | 5.08 |  |  |  | 7.14 | 10.15
2 | 50 | 60.3 | 2.77 |  | 3.18 | 3.91 | 3.91 |  | 5.54 | 5.54 |  |  |  | 8.74 | 11.07
2 1/2 | 65 | 73 | 3.05 |  | 4.78 | 5.16 | 5.16 |  | 7.01 | 7.01 |  |  |  | 9.53 | 14.02
3 | 80 | 88.9 | 3.05 |  | 4.78 | 5.49 | 5.49 |  | 7.62 | 7.62 |  |  |  | 11.13 | 15.24
3 1/2 | 90 | 101.6 | 3.05 |  | 4.78 | 5.74 | 5.74 |  | 8.08 | 8.08
4 | 100 | 114.3 | 3.05 |  | 4.78 | 6.02 | 6.02 |  | 8.56 | 8.56 |  | 11.13 |  | 13.49 | 17.12
5 | 125 | 141.3 | 3.4 |  |  | 6.55 | 6.55 |  | 9.53 | 9.53 |  | 12.7 |  | 15.88 | 19.05
6 | 150 | 168.3 | 3.4 |  |  | 7.11 | 7.11 |  | 10.97 | 10.97 |  | 14.27 |  | 18.26 | 21.95
8 | 200 | 219.1 | 3.76 | 6.35 | 7.04 | 8.18 | 8.18 | 10.31 | 12.7 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 22.23
10 | 250 | 273 | 4.19 | 6.35 | 7.8 | 9.27 | 9.27 | 12.7 | 15.09 | 12.7 | 18.26 | 21.44 | 25.4 | 28.58 | 25.4
12 | 300 | 323.8 | 4.57 | 6.35 | 8.38 | 10.31 | 9.53 | 14.27 | 17.48 | 12.7 | 21.44 | 25.4 | 28.58 | 33.32 | 25.4
14 | 350 | 355.6 | 6.35 | 7.92 | 9.53 | 11.13 | 9.53 | 15.09 | 19.05 | 12.7 | 23.83 | 27.79 | 31.75 | 35.71
16 | 400 | 406.4 | 6.35 | 7.92 | 9.53 | 12.7 | 9.53 | 16.66 | 21.44 | 12.7 | 26.19 | 30.96 | 36.53 | 40.49
18 | 450 | 457 | 6.35 | 7.92 | 11.13 | 14.27 | 9.53 | 19.05 | 23.83 | 12.7 | 29.36 | 34.93 | 39.67 | 45.24
20 | 500 | 508 | 6.35 | 9.53 | 12.7 | 15.09 | 9.53 | 20.62 | 26.19 | 12.7 | 32.54 | 38.1 | 44.45 | 50.01
22 | 550 | 559 | 6.35 | 9.53 | 12.7 |  | 9.53 | 22.23 | 28.58 | 12.7 | 34.93 | 41.28 | 47.63 | 53.98
24 | 600 | 610 | 6.35 | 9.53 | 14.27 | 17.48 | 9.53 | 24.61 | 30.96 | 12.7 | 38.89 | 46.02 | 52.37 | 59.54
Notes
• Blank cells mean that schedule is not listed for that size.
• STD equals Sch 40 up to NPS 10 and XS equals Sch 80 up to NPS 8.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Carbon Steel Pipe Schedule Chart (ASME B36.10M)
What this table is
Pipe schedule chart for welded and seamless carbon steel pipe, NPS 1/8 to 24, giving outside diameter and wall thickness in mm for every schedule.
Basis
ASME B36.10M Welded and Seamless Wrought Steel Pipe (metric values). Outside diameter is fixed for each NPS; the schedule sets the wall.
How to use
1. Find the nominal pipe size (NPS) or DN in the first columns.
2. Read across to the schedule; the value is the nominal wall thickness in mm.
3. Inside diameter = OD − 2 × wall. Mill tolerance on wall is usually −12.5 %.
Notes
Blank cells mean that schedule is not listed for that size.
STD equals Sch 40 up to NPS 10 and XS equals Sch 80 up to NPS 8.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/carbon-steel-pipe-schedule-chart/