## Table
Cv to Kv Conversion Table
Basis: Cv is US gallons per minute of water at 60 °F with 1 psi drop; Kv is m³/h of water at 5 to 40 °C with 1 bar drop. Kv = 0.865 Cv, Cv = 1.156 Kv (IEC 60534 1).
instrumentationblog.in/downloads/engineering-reference-tables/cv-to-kv-conversion-table/
Conversion in both directions
Cv | Kv | Kv | Cv
0.01 | 0.009 | 0.01 | 0.012
0.02 | 0.017 | 0.02 | 0.023
0.05 | 0.043 | 0.05 | 0.058
0.1 | 0.087 | 0.1 | 0.116
0.2 | 0.173 | 0.2 | 0.231
0.5 | 0.432 | 0.5 | 0.578
1 | 0.86 | 1 | 1.16
2 | 1.73 | 2 | 2.31
3 | 2.59 | 3 | 3.47
5 | 4.33 | 5 | 5.78
7.5 | 6.49 | 7.5 | 8.67
10 | 8.65 | 10 | 11.56
15 | 12.97 | 15 | 17.34
20 | 17.3 | 20 | 23.12
30 | 25.95 | 30 | 34.68
40 | 34.6 | 40 | 46.24
50 | 43.25 | 50 | 57.8
75 | 64.88 | 75 | 86.7
100 | 86.5 | 100 | 115.6
150 | 129.75 | 150 | 173.4
200 | 173 | 200 | 231.2
300 | 259.5 | 300 | 346.8
400 | 346 | 400 | 462.4
500 | 432.5 | 500 | 578
750 | 648.75 | 750 | 867
1000 | 865 | 1000 | 1156
1500 | 1297.5 | 1500 | 1734
2000 | 1730 | 2000 | 2312
Notes
• Coefficients scale linearly, so multiply for values between rows.
• Valve sizing for gas and flashing liquids needs the full IEC 60534 equations.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Cv to Kv Conversion Table
What this table is
Cv to Kv conversion table for control valve flow coefficients, both directions, for quick datasheet checks.
Basis
Cv is US gallons per minute of water at 60 °F with 1 psi drop; Kv is m³/h of water at 5 to 40 °C with 1 bar drop. Kv = 0.865 Cv, Cv = 1.156 Kv (IEC 60534 1).
How to use
1. Find the known coefficient in the first or third column.
2. Read the converted value next to it.
3. Liquid flow: Q (m³/h) = Kv × √(ΔP bar ÷ SG).
Notes
Coefficients scale linearly, so multiply for values between rows.
Valve sizing for gas and flashing liquids needs the full IEC 60534 equations.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/cv-to-kv-conversion-table/