## Table
Electrical Wire Colour Code Chart
Basis: IEC 60445 conductor identification, IEC 60204 1 machine control wiring, IEC 60079 14 for intrinsically safe circuits, IEC 60584 3 and ANSI MC96.1 for thermocouple cables.
instrumentationblog.in/downloads/engineering-reference-tables/electrical-wire-colour-code-chart/
AC power conductor colours
Standard or region | L1 | L2 | L3 | Neutral | Earth
IEC 60445 (Europe, India new) | Brown | Black | Grey | Blue | Green and yellow
India and UK old practice | Red | Yellow | Blue | Black | Green
USA 120/208 V (common) | Black | Red | Blue | White | Green or bare
USA 277/480 V (common) | Brown | Orange | Yellow | Grey or white | Green or bare
Canada | Red | Black | Blue | White | Green or bare
DC and control panel colours
Circuit | Colour
DC positive (IEC 60445) | Brown
DC negative (IEC 60445) | Grey
DC control circuits (IEC 60204 1) | Dark blue
AC control circuits (IEC 60204 1) | Red
Interlocks from external supply (IEC 60204 1) | Orange
Intrinsically safe circuits (IEC 60079 14) | Light blue
Protective earth | Green and yellow
Thermocouple extension cable colours (positive / negative)
Type | IEC 60584 3 | ANSI MC96.1 conductors | ANSI jacket
K | Green / white | Yellow / red | Yellow
J | Black / white | White / red | Black
T | Brown / white | Blue / red | Blue
E | Violet / white | Purple / red | Purple
N | Pink / white | Orange / red | Orange
R, S | Orange / white | Black / red | Green
B | Grey / white | Grey / red | Grey
Notes
• Old installations may use older colours; mark them when modifying circuits.
• Light blue for IS wiring is common practice; follow the site Ex dossier.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Electrical Wire Colour Code Chart
What this table is
Wire colour code chart for power, control panel and thermocouple wiring across the main standards used in plants.
Basis
IEC 60445 conductor identification, IEC 60204 1 machine control wiring, IEC 60079 14 for intrinsically safe circuits, IEC 60584 3 and ANSI MC96.1 for thermocouple cables.
How to use
1. Identify the standard used on your site.
2. Always prove dead with a tester; never rely on colour alone.
3. For thermocouples the IEC negative is always white; the ANSI negative is always red.
Notes
Old installations may use older colours; mark them when modifying circuits.
Light blue for IS wiring is common practice; follow the site Ex dossier.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/electrical-wire-colour-code-chart/