## Table
Hazardous Area Temperature Class Table (T1 to T6)
Basis: IEC 60079 0 temperature classification and NEC Article 500 subdivisions. A gas needs a T class whose maximum surface temperature is below its autoignition temperature.
instrumentationblog.in/downloads/engineering-reference-tables/hazardous-area-temperature-class-table/
Temperature classes
Class | Max surface °C | NEC subclasses (°C) | Example gases
T1 | 450 |  | Hydrogen, methane, propane, ammonia
T2 | 300 | T2A 280, T2B 260, T2C 230, T2D 215 | Acetylene, ethylene, butane, ethanol
T3 | 200 | T3A 180, T3B 165, T3C 160 | Petrol, diesel, kerosene, hexane, hydrogen sulphide
T4 | 135 | T4A 120 | Acetaldehyde, diethyl ether
T5 | 100 |  | Few common gases
T6 | 85 |  | Carbon disulphide
Notes
• Surface temperature limits are at the stated ambient range (usually −20 to 40 °C); hotter ambients may need derating.
• Check the gas data in IEC 60079 20 1 for your actual substances.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Hazardous Area Temperature Class Table (T1 to T6)
What this table is
Temperature class table giving the maximum surface temperature allowed for Ex equipment in each T class and typical gases that need it.
Basis
IEC 60079 0 temperature classification and NEC Article 500 subdivisions. A gas needs a T class whose maximum surface temperature is below its autoignition temperature.
How to use
1. Find the lowest autoignition temperature of the gases in the area.
2. Pick a class with a maximum surface temperature below it.
3. A T6 device is safe in a T1 to T5 area; not the reverse.
Notes
Surface temperature limits are at the stated ambient range (usually −20 to 40 °C); hotter ambients may need derating.
Check the gas data in IEC 60079 20 1 for your actual substances.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/hazardous-area-temperature-class-table/