## Table
Hazardous Area Zone and Gas Group Table
Basis: IEC 60079 10 1 and 10 2 area classification, IEC 60079 0 equipment groups and EPL, ATEX 2014/34/EU categories, NEC Articles 500 and 505.
instrumentationblog.in/downloads/engineering-reference-tables/hazardous-area-zone-gas-group-table/
Zones, EPL and equivalents
Zone | Definition | Presence | EPL | ATEX category | NEC equivalent
Zone 0 | Gas present continuously or for long periods | Over 1000 h per year (guide) | Ga | 1G | Class I Division 1
Zone 1 | Gas likely in normal operation | 10 to 1000 h per year (guide) | Gb | 2G | Class I Division 1
Zone 2 | Gas not likely; if present only briefly | Under 10 h per year (guide) | Gc | 3G | Class I Division 2
Zone 20 | Dust cloud present continuously |  | Da | 1D | Class II Division 1
Zone 21 | Dust cloud likely in normal operation |  | Db | 2D | Class II Division 1
Zone 22 | Dust cloud not likely; if present only briefly |  | Dc | 3D | Class II Division 2
Gas and dust groups
Group | Typical substance | NEC group | MESG (gas)
IIA | Propane, methane (mines are Group I) | D | Over 0.9 mm
IIB | Ethylene | C | 0.5 to 0.9 mm
IIC | Hydrogen, acetylene | B (hydrogen), A (acetylene) | Under 0.5 mm
IIIA | Combustible flyings | Class III
IIIB | Non conductive dust | Class II Group G
IIIC | Conductive dust | Class II Group E
Notes
• Hour figures are common guidance, not part of the definitions.
• IIC equipment may be used in IIB and IIA areas; not the reverse.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Hazardous Area Zone and Gas Group Table
What this table is
Hazardous area zone table linking IEC zones, equipment protection levels, ATEX categories and North American divisions, plus gas and dust groups.
Basis
IEC 60079 10 1 and 10 2 area classification, IEC 60079 0 equipment groups and EPL, ATEX 2014/34/EU categories, NEC Articles 500 and 505.
How to use
1. Get the zone and group from the area classification drawing.
2. Pick equipment with an EPL at least equal to the zone and a group at least equal to the gas.
3. Check the temperature class as well.
Notes
Hour figures are common guidance, not part of the definitions.
IIC equipment may be used in IIB and IIA areas; not the reverse.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/hazardous-area-zone-gas-group-table/