## Table
ISA Instrument Letter Codes Table (ISA 5.1)
Basis: ANSI/ISA 5.1 Instrumentation Symbols and Identification. 'User's choice' letters must be defined in the project legend.
instrumentationblog.in/downloads/engineering-reference-tables/isa-instrument-letter-codes-table/
ISA 5.1 identification letters
Letter | First letter (measured variable) | Succeeding letter (function) | Modifier
A | Analysis | Alarm
B | Burner, combustion | User's choice | User's choice
C | User's choice | Control | Close
D | User's choice |  | Differential (modifier)
E | Voltage | Sensor, primary element
F | Flow |  | Ratio (modifier)
G | User's choice | Glass, gauge, viewing device
H | Hand |  | High
I | Current | Indicate
J | Power |  | Scan (modifier)
K | Time, schedule | Control station | Time rate of change (modifier)
L | Level | Light | Low
M | User's choice |  | Middle, intermediate
N | User's choice | User's choice | User's choice
O | User's choice | Orifice, restriction | Open
P | Pressure | Point (test connection)
Q | Quantity | Integrate, totalise | Integrate (modifier)
R | Radiation | Record | Run
S | Speed, frequency | Switch | Safety (modifier), stop
T | Temperature | Transmit
U | Multivariable | Multifunction
V | Vibration, machine analysis | Valve, damper, louver
W | Weight, force | Well, probe
X | Unclassified | Unclassified | Unclassified
Y | Event, state, presence | Relay, compute, convert
Z | Position, dimension | Driver, actuator
Common tag examples
Tag | Meaning
PT | Pressure transmitter
FT | Flow transmitter
LT | Level transmitter
TT | Temperature transmitter
PDT | Differential pressure transmitter
FE | Flow element (orifice, meter body)
TE | Temperature element (RTD, thermocouple)
PI | Pressure indicator (gauge)
LG | Level gauge (sight glass)
FIC | Flow indicating controller
LIC | Level indicating controller
FCV | Flow control valve
PSV | Pressure safety valve
XV | On off valve
LSHH | Level switch high high
PAL | Pressure alarm low
TW | Thermowell
FQI | Flow totaliser indicator
ZSO | Position switch open
SDV | Shutdown valve (common practice)
Notes
• SDV, ESDV and similar tags are common practice rather than strict ISA 5.1.
• Check the project P&ID legend for user's choice letters.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: ISA Instrument Letter Codes Table (ISA 5.1)
What this table is
Instrument letter codes table for reading and writing P&ID tag numbers, with the meaning of each letter in first and succeeding positions.
Basis
ANSI/ISA 5.1 Instrumentation Symbols and Identification. 'User's choice' letters must be defined in the project legend.
How to use
1. The first letter is the measured or initiating variable.
2. Following letters are readout or output functions.
3. Modifiers (D, F, H, L, S) refine the letter before them.
Notes
SDV, ESDV and similar tags are common practice rather than strict ISA 5.1.
Check the project P&ID legend for user's choice letters.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/isa-instrument-letter-codes-table/