## Table
Metric Cable Size and Resistance Table (IEC 60228)
Basis: IEC 60228 Table 2, maximum DC resistance at 20 °C for class 2 plain copper and aluminium conductors (aluminium from 10 mm²).
instrumentationblog.in/downloads/engineering-reference-tables/metric-cable-size-resistance-table/
Conductor resistance at 20 °C
Size mm² | Copper Ω/km | Aluminium Ω/km | Cu loop Ω per 100 m | Nearest AWG
0.5 | 36 |  | 7.2 | 20
0.75 | 24.5 |  | 4.9 | 18
1 | 18.1 |  | 3.62 | 17
1.5 | 12.1 |  | 2.42 | 15
2.5 | 7.41 |  | 1.482 | 13
4 | 4.61 |  | 0.922 | 11
6 | 3.08 |  | 0.616 | 9
10 | 1.83 | 3.08 | 0.366 | 7
16 | 1.15 | 1.91 | 0.23 | 5
25 | 0.727 | 1.2 | 0.145 | 3
35 | 0.524 | 0.868 | 0.105 | 2
50 | 0.387 | 0.641 | 0.0774 | 1/0
70 | 0.268 | 0.443 | 0.0536 | 2/0
95 | 0.193 | 0.32 | 0.0386 | 3/0
120 | 0.153 | 0.253 | 0.0306 | 4/0
150 | 0.124 | 0.206 | 0.0248 | > 4/0
185 | 0.0991 | 0.164 | 0.0198 | > 4/0
240 | 0.0754 | 0.125 | 0.0151 | > 4/0
300 | 0.0601 | 0.1 | 0.012 | > 4/0
Notes
• Values are maximum limits; real cables are usually a little lower.
• Instrument loops: check the transmitter minimum voltage with the loop resistance.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Metric Cable Size and Resistance Table (IEC 60228)
What this table is
Cable size chart for metric conductors with the maximum DC resistance allowed by IEC 60228 for class 2 stranded conductors.
Basis
IEC 60228 Table 2, maximum DC resistance at 20 °C for class 2 plain copper and aluminium conductors (aluminium from 10 mm²).
How to use
1. Find the conductor size.
2. Multiply Ω/km by route length in km × 2 for the loop resistance.
3. Correct for temperature: R rises about 0.393 % per °C for copper.
Notes
Values are maximum limits; real cables are usually a little lower.
Instrument loops: check the transmitter minimum voltage with the loop resistance.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/metric-cable-size-resistance-table/