## Table
Motor Full Load Current Table (3 Phase)
Basis: NFPA 70 (NEC) Table 430.250, full load current for three phase induction motors running at usual speeds with normal torque characteristics.
instrumentationblog.in/downloads/engineering-reference-tables/motor-full-load-current-table/
Full load current in amperes
hp | kW | 208 V | 230 V | 460 V | 575 V
1/2 | 0.37 | 2.4 | 2.2 | 1.1 | 0.9
3/4 | 0.56 | 3.5 | 3.2 | 1.6 | 1.3
1 | 0.75 | 4.6 | 4.2 | 2.1 | 1.7
1 1/2 | 1.12 | 6.6 | 6 | 3 | 2.4
2 | 1.49 | 7.5 | 6.8 | 3.4 | 2.7
3 | 2.24 | 10.6 | 9.6 | 4.8 | 3.9
5 | 3.73 | 16.7 | 15.2 | 7.6 | 6.1
7 1/2 | 5.59 | 24.2 | 22 | 11 | 9
10 | 7.46 | 30.8 | 28 | 14 | 11
15 | 11.19 | 46.2 | 42 | 21 | 17
20 | 14.91 | 59.4 | 54 | 27 | 22
25 | 18.64 | 74.8 | 68 | 34 | 27
30 | 22.37 | 88 | 80 | 40 | 32
40 | 29.83 | 114 | 104 | 52 | 41
50 | 37.29 | 143 | 130 | 65 | 52
60 | 44.74 | 169 | 154 | 77 | 62
75 | 55.93 | 211 | 192 | 96 | 77
100 | 74.57 | 273 | 248 | 124 | 99
125 | 93.21 | 343 | 312 | 156 | 125
150 | 111.86 | 396 | 360 | 180 | 144
200 | 149.14 | 528 | 480 | 240 | 192
Notes
• For 220 to 240 V use the 230 V column; 440 to 480 V use 460 V; 550 to 600 V use 575 V.
• IEC motors at 400 to 415 V draw roughly 10 to 15 % more current than the 460 V values; always check the nameplate.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Motor Full Load Current Table (3 Phase)
What this table is
Motor full load current table for three phase squirrel cage induction motors, used to size conductors, fuses and overload protection.
Basis
NFPA 70 (NEC) Table 430.250, full load current for three phase induction motors running at usual speeds with normal torque characteristics.
How to use
1. Find the motor hp (or nearest kW).
2. Read the current at the supply voltage.
3. Use the table for conductor and short circuit protection; set overloads from the nameplate.
Notes
For 220 to 240 V use the 230 V column; 440 to 480 V use 460 V; 550 to 600 V use 575 V.
IEC motors at 400 to 415 V draw roughly 10 to 15 % more current than the 460 V values; always check the nameplate.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/motor-full-load-current-table/