## Table
NEMA Enclosure Types Chart (NEMA 250)
Basis: NEMA 250 Enclosures for Electrical Equipment (1000 V maximum). Types 7, 8, 9 and 10 cover hazardous locations and mines.
instrumentationblog.in/downloads/engineering-reference-tables/nema-enclosure-types-chart/
NEMA enclosure types
Type | Location | Protects against | Approx. IP (one way)
1 | Indoor | Falling dirt, accidental contact | IP10
2 | Indoor | Plus dripping and light splashing water | IP11
3 | Indoor or outdoor | Rain, sleet, snow, windblown dust; external ice | IP54
3R | Indoor or outdoor | Rain, sleet, snow; external ice | IP14
3S | Indoor or outdoor | As 3, and mechanism works when iced | IP54
3X, 3RX, 3SX | Indoor or outdoor | As 3, 3R, 3S plus corrosion resistance
4 | Indoor or outdoor | Hose directed water, windblown dust, rain | IP66
4X | Indoor or outdoor | As 4 plus corrosion resistance | IP66
5 | Indoor | Settling dust, lint, fibres; dripping liquids | IP52
6 | Indoor or outdoor | Temporary submersion at limited depth | IP67
6P | Indoor or outdoor | Prolonged submersion at limited depth | IP68
7 | Indoor | Hazardous locations, Class I Div 1 gases (explosion proof)
8 | Indoor or outdoor | Hazardous locations, Class I gases, oil immersed
9 | Indoor | Hazardous locations, Class II combustible dust
10 | Mines | Mine Safety and Health Administration requirements
12, 12K | Indoor | Dust, lint, fibres, dripping oil and coolant (no knockouts) | IP52
13 | Indoor | Dust, spraying water, oil and non corrosive coolant | IP54
Notes
• A NEMA type meets or exceeds the IP shown, but an IP rating does not prove a NEMA type (NEMA also tests corrosion, icing and construction).
• Types 7 and 9 are hazardous location enclosures and need third party certification.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: NEMA Enclosure Types Chart (NEMA 250)
What this table is
NEMA enclosure types chart summarising where each NEMA 250 enclosure type can be used and what it protects against.
Basis
NEMA 250 Enclosures for Electrical Equipment (1000 V maximum). Types 7, 8, 9 and 10 cover hazardous locations and mines.
How to use
1. Choose the type that covers the location (indoor or outdoor) and hazards.
2. Use 4X for washdown or corrosive sites.
3. Use the IP column only as a rough guide.
Notes
A NEMA type meets or exceeds the IP shown, but an IP rating does not prove a NEMA type (NEMA also tests corrosion, icing and construction).
Types 7 and 9 are hazardous location enclosures and need third party certification.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/nema-enclosure-types-chart/