## Table
NEMA to IP Conversion Chart
Basis: NEMA 250 Annex comparison with IEC 60529. The comparison is one way: NEMA type to IP code.
instrumentationblog.in/downloads/engineering-reference-tables/nema-to-ip-conversion-chart/
NEMA type to minimum IP equivalent
NEMA type | Meets or exceeds
1 | IP10
2 | IP11
3 | IP54
3R | IP14
3S | IP54
4 | IP66
4X | IP66
5 | IP52
6 | IP67
6P | IP68
12 | IP52
12K | IP52
13 | IP54
Notes
• Hazardous location types 7 to 10 have no IP equivalent.
• NEMA's own comparison is more conservative for some types (for example IP56 for Type 4 and 4X); many makers test 4X enclosures to IP66.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: NEMA to IP Conversion Chart
What this table is
NEMA to IP conversion chart showing the IP rating each NEMA enclosure type meets or exceeds.
Basis
NEMA 250 Annex comparison with IEC 60529. The comparison is one way: NEMA type to IP code.
How to use
1. Find the NEMA type on the enclosure.
2. Read the IP code it meets or exceeds.
3. Do not convert IP to NEMA: IP tests do not cover corrosion, icing or gasket ageing.
Notes
Hazardous location types 7 to 10 have no IP equivalent.
NEMA's own comparison is more conservative for some types (for example IP56 for Type 4 and 4X); many makers test 4X enclosures to IP66.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/nema-to-ip-conversion-chart/