## Table
NPS to DN Pipe Size Chart
Basis: ISO 6708 DN designations and ASME B36.10M / B36.19M outside diameters.
instrumentationblog.in/downloads/engineering-reference-tables/nps-to-dn-pipe-size-chart/
NPS, DN and outside diameter
NPS (inch) | DN | OD mm | OD inch
1/8 | 6 | 10.3 | 0.406
1/4 | 8 | 13.7 | 0.539
3/8 | 10 | 17.1 | 0.673
1/2 | 15 | 21.3 | 0.839
3/4 | 20 | 26.7 | 1.051
1 | 25 | 33.4 | 1.315
1 1/4 | 32 | 42.2 | 1.661
1 1/2 | 40 | 48.3 | 1.902
2 | 50 | 60.3 | 2.374
2 1/2 | 65 | 73 | 2.874
3 | 80 | 88.9 | 3.5
3 1/2 | 90 | 101.6 | 4
4 | 100 | 114.3 | 4.5
5 | 125 | 141.3 | 5.563
6 | 150 | 168.3 | 6.626
8 | 200 | 219.1 | 8.626
10 | 250 | 273 | 10.748
12 | 300 | 323.8 | 12.748
14 | 350 | 355.6 | 14
16 | 400 | 406.4 | 16
18 | 450 | 457 | 17.992
20 | 500 | 508 | 20
22 | 550 | 559 | 22.008
24 | 600 | 610 | 24.016
Notes
• From NPS 14 the OD in inches equals the NPS.
• EN 10255 and some metric tube systems use different ODs for the same DN.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: NPS to DN Pipe Size Chart
What this table is
NPS to DN chart for steel pipe, with the actual outside diameter in mm and inches for each size.
Basis
ISO 6708 DN designations and ASME B36.10M / B36.19M outside diameters.
How to use
1. Find NPS in inches and read the DN.
2. Use the OD for clamp on meters, flange and fitting selection.
3. DN is a label; it is not the bore.
Notes
From NPS 14 the OD in inches equals the NPS.
EN 10255 and some metric tube systems use different ODs for the same DN.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/nps-to-dn-pipe-size-chart/