## Table
SIL Level PFD and RRF Table (IEC 61508)
Basis: IEC 61508 1 Tables 2 and 3, and IEC 61511 1 (2016) Table 6 minimum hardware fault tolerance for safety instrumented functions.
instrumentationblog.in/downloads/engineering-reference-tables/sil-level-pfd-table/
SIL targets
SIL | PFDavg (low demand) | Risk reduction factor | PFH per hour (high demand)
SIL 4 | ≥ 10−⁵ to < 10−⁴ | > 10,000 to ≤ 100,000 | ≥ 10−⁹ to < 10−⁸
SIL 3 | ≥ 10−⁴ to < 10−³ | > 1,000 to ≤ 10,000 | ≥ 10−⁸ to < 10−⁷
SIL 2 | ≥ 10−³ to < 10−² | > 100 to ≤ 1,000 | ≥ 10−⁷ to < 10−⁶
SIL 1 | ≥ 10−² to < 10−¹ | > 10 to ≤ 100 | ≥ 10−⁶ to < 10−⁵
Minimum hardware fault tolerance (IEC 61511 1:2016)
SIL | Low demand HFT | High or continuous demand HFT
SIL 1 | 0 | 0
SIL 2 | 0 | 1
SIL 3 | 1 | 2
SIL 4 | 2 | Not allowed
Notes
• Low demand means a demand less than once per year.
• IEC 61511 SIL 4 is rarely used in the process industry.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: SIL Level PFD and RRF Table (IEC 61508)
What this table is
SIL level table showing the target failure measures for each safety integrity level in low demand and high or continuous demand modes.
Basis
IEC 61508 1 Tables 2 and 3, and IEC 61511 1 (2016) Table 6 minimum hardware fault tolerance for safety instrumented functions.
How to use
1. Get the required SIL from the hazard and risk assessment (LOPA, risk graph).
2. Verify that the SIF PFDavg falls inside the band.
3. Check architecture (HFT) and systematic capability too.
Notes
Low demand means a demand less than once per year.
IEC 61511 SIL 4 is rarely used in the process industry.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/sil-level-pfd-table/