## Table
Square Root Flow and DP Table
Basis: Flow is proportional to the square root of differential pressure: Q% = 10 × √(DP%), DP% = Q%² ÷ 100.
instrumentationblog.in/downloads/engineering-reference-tables/square-root-flow-dp-table/
DP percent to flow percent
DP % | Flow % | Linear DP output mA | Square rooted output mA
0 | 0 | 4 | 4
1 | 10 | 4.16 | 5.6
2 | 14.14 | 4.32 | 6.263
4 | 20 | 4.64 | 7.2
5 | 22.36 | 4.8 | 7.578
9 | 30 | 5.44 | 8.8
10 | 31.62 | 5.6 | 9.06
16 | 40 | 6.56 | 10.4
20 | 44.72 | 7.2 | 11.155
25 | 50 | 8 | 12
30 | 54.77 | 8.8 | 12.764
36 | 60 | 9.76 | 13.6
40 | 63.25 | 10.4 | 14.119
49 | 70 | 11.84 | 15.2
50 | 70.71 | 12 | 15.314
60 | 77.46 | 13.6 | 16.394
64 | 80 | 14.24 | 16.8
70 | 83.67 | 15.2 | 17.387
80 | 89.44 | 16.8 | 18.311
81 | 90 | 16.96 | 18.4
90 | 94.87 | 18.4 | 19.179
100 | 100 | 20 | 20
Flow percent to DP percent
Flow % | DP % | Linear DP output mA | Square rooted output mA
0 | 0 | 4 | 4
5 | 0.25 | 4.04 | 4.8
10 | 1 | 4.16 | 5.6
15 | 2.25 | 4.36 | 6.4
20 | 4 | 4.64 | 7.2
25 | 6.25 | 5 | 8
30 | 9 | 5.44 | 8.8
35 | 12.25 | 5.96 | 9.6
40 | 16 | 6.56 | 10.4
45 | 20.25 | 7.24 | 11.2
50 | 25 | 8 | 12
55 | 30.25 | 8.84 | 12.8
60 | 36 | 9.76 | 13.6
65 | 42.25 | 10.76 | 14.4
70 | 49 | 11.84 | 15.2
75 | 56.25 | 13 | 16
80 | 64 | 14.24 | 16.8
85 | 72.25 | 15.56 | 17.6
90 | 81 | 16.96 | 18.4
95 | 90.25 | 18.44 | 19.2
100 | 100 | 20 | 20
Notes
• Below about 10 % flow (1 % DP) the signal is very sensitive to zero errors; most systems apply low flow cut off.
• Doubling the flow needs four times the DP.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Square Root Flow and DP Table
What this table is
Square root flow table for orifice, venturi and other DP flow elements, linking differential pressure, flow and transmitter output.
Basis
Flow is proportional to the square root of differential pressure: Q% = 10 × √(DP%), DP% = Q%² ÷ 100.
How to use
1. Know whether square root is done in the transmitter or the DCS: only once.
2. For a linear DP transmitter, use the 'Linear DP output' column.
3. For a transmitter with square root on, use the 'Square rooted output' column.
Notes
Below about 10 % flow (1 % DP) the signal is very sensitive to zero errors; most systems apply low flow cut off.
Doubling the flow needs four times the DP.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/square-root-flow-dp-table/