## Table
Stainless Steel Pipe Schedule Chart (ASME B36.19M)
Basis: ASME B36.19M Stainless Steel Pipe (metric values). OD is the same as carbon steel pipe of the same NPS.
instrumentationblog.in/downloads/engineering-reference-tables/stainless-steel-pipe-schedule-chart/
Stainless steel wall thickness in mm
NPS | DN | OD mm | Sch 5S | Sch 10S | Sch 40S | Sch 80S
1/8 | 6 | 10.3 |  | 1.24 | 1.73 | 2.41
1/4 | 8 | 13.7 |  | 1.65 | 2.24 | 3.02
3/8 | 10 | 17.1 |  | 1.65 | 2.31 | 3.2
1/2 | 15 | 21.3 | 1.65 | 2.11 | 2.77 | 3.73
3/4 | 20 | 26.7 | 1.65 | 2.11 | 2.87 | 3.91
1 | 25 | 33.4 | 1.65 | 2.77 | 3.38 | 4.55
1 1/4 | 32 | 42.2 | 1.65 | 2.77 | 3.56 | 4.85
1 1/2 | 40 | 48.3 | 1.65 | 2.77 | 3.68 | 5.08
2 | 50 | 60.3 | 1.65 | 2.77 | 3.91 | 5.54
2 1/2 | 65 | 73 | 2.11 | 3.05 | 5.16 | 7.01
3 | 80 | 88.9 | 2.11 | 3.05 | 5.49 | 7.62
3 1/2 | 90 | 101.6 | 2.11 | 3.05 | 5.74 | 8.08
4 | 100 | 114.3 | 2.11 | 3.05 | 6.02 | 8.56
5 | 125 | 141.3 | 2.77 | 3.4 | 6.55 | 9.53
6 | 150 | 168.3 | 2.77 | 3.4 | 7.11 | 10.97
8 | 200 | 219.1 | 2.77 | 3.76 | 8.18 | 12.7
10 | 250 | 273 | 3.4 | 4.19 | 9.27 | 12.7
12 | 300 | 323.8 | 3.96 | 4.57 | 9.53 | 12.7
14 | 350 | 355.6 | 3.96 | 4.78 | 9.53 | 12.7
16 | 400 | 406.4 | 4.19 | 4.78 | 9.53 | 12.7
18 | 450 | 457 | 4.19 | 4.78 | 9.53 | 12.7
20 | 500 | 508 | 4.78 | 5.54 | 9.53 | 12.7
22 | 550 | 559 | 4.78 | 5.54
24 | 600 | 610 | 5.54 | 6.35 | 9.53 | 12.7
Notes
• 40S and 80S match Sch 40 and Sch 80 up to NPS 10 (8 for 80S); larger sizes differ.
• Blank cells are not listed in B36.19M.
Free download from instrumentationblog.in. Check values against the current edition of the standard for design work.

## How to Use
How to use: Stainless Steel Pipe Schedule Chart (ASME B36.19M)
What this table is
Stainless steel pipe schedule chart for Sch 5S, 10S, 40S and 80S with outside diameter and wall thickness in mm.
Basis
ASME B36.19M Stainless Steel Pipe (metric values). OD is the same as carbon steel pipe of the same NPS.
How to use
1. Find the NPS or DN.
2. Read across to the schedule for the wall thickness in mm.
3. Inside diameter = OD − 2 × wall.
Notes
40S and 80S match Sch 40 and Sch 80 up to NPS 10 (8 for 80S); larger sizes differ.
Blank cells are not listed in B36.19M.
Online version: https://instrumentationblog.in/downloads/engineering-reference-tables/stainless-steel-pipe-schedule-chart/