## How to Use
HOW TO USE: ALARM RATIONALISATION AND PRIORITY WORKSHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. List alarms from the DCS.
2. For each, agree the worst consequence without operator action and the time available.
3. Priority is calculated; adjust the matrix to your philosophy if needed.
4. Record the operator action and decide keep, remove or change.
5. Compare the distribution with the guideline.
What the formulas do
• Score = severity rank (1 to 3) + urgency rank (1 to 3).
• High ≥ 5, Medium = 4, Low ≤ 3.
• Distribution = count per priority ÷ total.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Example priority matrix (edit to your alarm philosophy): High when severity and urgency together score 5 or more, Medium at 4, Low otherwise. Distribution guidance about 80 % low, 15 % medium, 5 % high (ISA 18.2 / EEMUA 191).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
ALARM RATIONALISATION AND PRIORITY WORKSHEET
Project: Boiler 3 alarm review |  |  |  |  | Calc no: CALC ALM 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Review
Unit |  | Boiler 3 |  |  | Alarm philosophy |  | APH 001 rev 2
Team |  | Operations, process, instrument
Alarms
Alarm tag | Description | Severity | Time to respond | Score | Priority | Operator action | Keep? | Set point | Remarks
PAHH 1101 | Steam header very high pressure | Severe | Under 5 min | 6 | High |  | Keep
LAL 2101 | Drum level low | Severe | 5 to 15 min | 5 | High |  | Keep
TAH 3105 | Bearing temperature high | Major | 5 to 15 min | 4 | Medium |  | Keep
FAL 4102 | Cooling water flow low | Major | 15 to 30 min | 3 | Low |  | Keep
PAL 5101 | Instrument air pressure low | Major | Under 5 min | 5 | High |  | Keep
AAH 6101 | Effluent pH high | Minor | 15 to 30 min | 2 | Low |  | Keep
LAH 7101 | Day tank level high | Minor | 5 to 15 min | 3 | Low |  | Keep
High priority (%) | [7 empty] | 42.8571
Medium priority (%) | [7 empty] | 14.2857
Low priority (%) | [7 empty] | 42.8571
Alarms marked for removal | [7 empty] | 0
Every alarm must have a defined operator action and enough time to take it. Alarms without an action are candidates for removal or conversion to events.
Rationalisation lead |  |  |  |  | Operations
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: