## How to Use
HOW TO USE: 4 TO 20 MA ANALOG SCALING TABLE
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter range, unit and raw count limits of your input card.
2. Choose square root for DP flow loops.
3. Set the low flow cutoff.
4. Use the table for loop checks and HMI verification.
What the formulas do
• mA = 4 + 16 × p.
• Raw = raw min + (raw max − raw min) × p.
• Value = LRV + span × p, or × √p for square root.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: mA = 4 + 16 × %; raw = raw min + (raw max − raw min) × %; value = LRV + span × % (or × √% for square root).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
4 TO 20 MA ANALOG SCALING TABLE
Project: FT 3105 scaling |  |  | Calc no: CALC AI 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Loop data
LRV (engineering units) |  | 0 | URV (engineering units) |  | 50
Unit |  | m³/h | Raw count at 4 mA |  | 0
Raw count at 20 mA |  | 27648 | Square root (DP flow)? |  | Yes
Low flow cutoff (% of flow) |  | 5
Scaling table
Signal (% of span) | Current (mA) | Raw counts | Value (units) | Value (% of range) | Displayed | Notes
0 | 4 | 0 | 0 | 0 | 0 (cutoff)
5 | 4.8 | 1382 | 11.1803 | 22.3607 | 11.18
10 | 5.6 | 2765 | 15.8114 | 31.6228 | 15.81
20 | 7.2 | 5530 | 22.3607 | 44.7214 | 22.36
25 | 8 | 6912 | 25 | 50 | 25.00
30 | 8.8 | 8294 | 27.3861 | 54.7723 | 27.39
40 | 10.4 | 11059 | 31.6228 | 63.2456 | 31.62
50 | 12 | 13824 | 35.3553 | 70.7107 | 35.36
60 | 13.6 | 16589 | 38.7298 | 77.4597 | 38.73
70 | 15.2 | 19354 | 41.833 | 83.666 | 41.83
75 | 16 | 20736 | 43.3013 | 86.6025 | 43.30
80 | 16.8 | 22118 | 44.7214 | 89.4427 | 44.72
90 | 18.4 | 24883 | 47.4342 | 94.8683 | 47.43
100 | 20 | 27648 | 50 | 100 | 50.00
Siemens S7 uses 0 to 27648 for 0 to 100 %; other PLCs use 0 to 32767, 4000 to 20000 or 0 to 65535. Apply square root only once, in the transmitter or the PLC.
Prepared by |  |  | Checked by
Name: |  |  | Name:
Signature: |  |  | Signature:
Date: |  |  | Date: