## How to Use
HOW TO USE: CABLE VOLTAGE DROP AND SIZE SELECTION CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Select the system and enter voltage, current, power factor and route length.
2. Choose copper or aluminium and the conductor operating temperature (70 °C PVC, 90 °C XLPE).
3. Set the allowed voltage drop (often 3 % for lighting and 5 % for power, per project).
4. Read the smallest size within the limit, then confirm its current rating for your installation method.
What the formulas do
• R at temperature = R20 × (1 + α (T − 20)), α = 0.00393 (Cu) or 0.00403 (Al).
• ΔV = k × I × L × (R cos φ + X sin φ) ÷ 1000.
• Smallest size = first row with ΔV % within the limit (INDEX and MATCH).
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Conductor resistances from IEC 60228 (class 2, at 20 °C), corrected to operating temperature. Current carrying capacity is not checked: confirm it with IEC 60364-5-52 or your cable data.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
CABLE VOLTAGE DROP AND SIZE SELECTION CALCULATOR
Project: Pump P 101 feeder |  |  |  | Calc no: CALC EL 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Circuit
System |  | Three phase |  | Voltage (V, line to line for 3 phase) |  | 415
Load current (A) |  | 45 |  | Power factor |  | 0.85
Route length, one way (m) |  | 120 |  | Conductor |  | Copper
Conductor temperature (°C) |  | 70 |  | Allowed voltage drop (%) |  | 3
Reactance (Ω/km) |  | 0.08
Voltage drop for each size
Size (mm²) | Copper R20 (Ω/km) | Aluminium R20 (Ω/km) | R at temperature (Ω/km) | Voltage drop (V) | Voltage drop (%) | Within limit
1.5 | 12.1 |  | 14.4777 | 115.4931 | 27.8297 | CHECK
2.5 | 7.41 |  | 8.8661 | 70.8804 | 17.0796 | CHECK
4 | 4.61 |  | 5.5159 | 44.2459 | 10.6617 | CHECK
6 | 3.08 |  | 3.6852 | 29.6921 | 7.1547 | CHECK
10 | 1.83 |  | 2.1896 | 17.8017 | 4.2896 | CHECK
16 | 1.15 | 1.91 | 1.376 | 11.3333 | 2.7309 | OK
25 | 0.727 | 1.2 | 0.86986 | 7.3096 | 1.7614 | OK
35 | 0.524 | 0.868 | 0.62697 | 5.3786 | 1.2961 | OK
50 | 0.387 | 0.641 | 0.46305 | 4.0754 | 0.98203 | OK
70 | 0.268 | 0.443 | 0.32066 | 2.9435 | 0.70927 | OK
95 | 0.193 | 0.32 | 0.23092 | 2.23 | 0.53736 | OK
120 | 0.153 | 0.253 | 0.18306 | 1.8495 | 0.44567 | OK
150 | 0.124 | 0.206 | 0.14837 | 1.5737 | 0.3792 | OK
185 | 0.0991 | 0.164 | 0.11857 | 1.3368 | 0.32213 | OK
240 | 0.0754 | 0.125 | 0.090216 | 1.1114 | 0.26781 | OK
300 | 0.0601 | 0.1 | 0.07191 | 0.96585 | 0.23274 | OK
Smallest size within the voltage drop limit (mm²) | [5 empty] | 16
Voltage drop with that size (%) | [5 empty] | 2.7309
ΔV = k × I × L × (R cos φ + X sin φ) with k = √3 for three phase and 2 for single phase and DC. Always also check current rating, short circuit withstand and earth fault loop impedance.
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: