## How to Use
HOW TO USE: CONTROL VALVE SIZING CALCULATOR (LIQUID)
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the fluid specific gravity, vapour pressure and critical pressure (water: Pc = 220.64 bar a).
2. Enter FL from the valve manufacturer (globe valves about 0.9, ball and butterfly lower).
3. Fill in flow and inlet and outlet pressure (absolute) for the minimum, normal and maximum cases.
4. Read the required Kv and Cv. If a case shows CHOKED, the sizing ΔP is limited to the choked value and the valve may cavitate.
5. Enter the rated Cv of the valve you are considering and check the Cv ratios at maximum and minimum flow.
What the formulas do
• ΔP = P1 − P2; choked ΔP = FL² × (P1 − FF × Pv).
• Sizing ΔP = smaller of ΔP and choked ΔP.
• Kv = Q × √(SG ÷ ΔP<sub>sizing</sub>), Cv = 1.156 × Kv.
• Cv ratio = required Cv ÷ rated Cv; aim for about 0.1 to 0.85 across the range.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: IEC 60534-2-1 liquid sizing equations for turbulent, non choked and choked flow (pipe geometry factor FP taken as 1).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
CONTROL VALVE SIZING CALCULATOR (LIQUID)
Project: Feed pump discharge FV 3101 |  |  |  |  | Calc no: CALC CV 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Fluid and valve data
Specific gravity (water = 1) |  | 1 |  |  | Vapour pressure Pv (bar a) |  | 0.0317
Critical pressure Pc (bar a) |  | 220.64 |  |  | Liquid recovery factor FL |  | 0.9
Rated Cv of selected valve |  | 108 |  |  | Selected valve |  | Globe, 3", equal %
FF (calculated) |  | 0.95664 |  |  | Rated Kv (calculated) |  | 93.4256
Sizing cases (pressures in bar a)
Case | Flow Q (m³/h) | Inlet P1 | Outlet P2 | ΔP (bar) | Choked ΔP (bar) | Sizing ΔP (bar) | Required Kv | Required Cv | Cv ratio (req ÷ rated) | Flow regime
Minimum | 20 | 9 | 6.5 | 2.5 | 7.2654 | 2.5 | 12.6491 | 14.6224 | 0.13539 | OK
Normal | 60 | 8 | 6.2 | 1.8 | 6.4554 | 1.8 | 44.7214 | 51.6979 | 0.47868 | OK
Maximum | 85 | 7.5 | 6 | 1.5 | 6.0504 | 1.5 | 69.4022 | 80.229 | 0.74286 | OK
Cv ratio at maximum flow (target ≤ 0.85) | [8 empty] | OK
Cv ratio at minimum flow (target ≥ 0.1) | [8 empty] | OK
Cv = 1.156 × Kv. Kv = Q × √(SG ÷ ΔP). Choked ΔP = FL² × (P1 − FF × Pv), FF = 0.96 − 0.28 √(Pv ÷ Pc). Check noise and cavitation separately for high ΔP services.
Prepared by |  |  |  |  | Checked by
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: