## How to Use
HOW TO USE: DP FLOW TRANSMITTER RERANGE CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter present maximum flow and DP.
2. Enter the new maximum flow and transmitter URL.
3. Read the new DP span and URL check.
4. Use the table to set and test the transmitter.
5. Update all related documents and settings.
What the formulas do
• DP_new = DP_old × (Q_new ÷ Q_old)².
• DP % = (flow %)².
• mA linear = 4 + 16 × DP %; mA square root = 4 + 16 × flow %.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: For a fixed orifice and fluid, DP ∝ Q²: DP_new = DP_old × (Q_new ÷ Q_old)². Flow % = √(DP %). Coefficient changes with Reynolds number are neglected; resize the orifice for large changes.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
DP FLOW TRANSMITTER RERANGE CALCULATOR
Project: FT 3105 rerange |  |  | Calc no: CALC FT 005 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Present and new range
Present maximum flow |  | 40 | Present DP at maximum (mbar) |  | 250
New maximum flow |  | 50 | Transmitter URL (mbar) |  | 620
New DP at maximum (mbar) |  | 390.625 | URL check |  | OK, within URL
Turndown on sensor (URL ÷ span) |  | 1.5872
New range table
Flow (% of new max) | Flow | DP (mbar) | DP (% of span) | mA (linear transmitter) | mA (square root transmitter) | Notes
0 | 0 | 0 | 0 | 4 | 4
10 | 5 | 3.9062 | 1 | 4.16 | 5.6
20 | 10 | 15.625 | 4 | 4.64 | 7.2
30 | 15 | 35.1562 | 9 | 5.44 | 8.8
40 | 20 | 62.5 | 16 | 6.56 | 10.4
50 | 25 | 97.6562 | 25 | 8 | 12
60 | 30 | 140.625 | 36 | 9.76 | 13.6
70 | 35 | 191.4062 | 49 | 11.84 | 15.2
80 | 40 | 250 | 64 | 14.24 | 16.8
90 | 45 | 316.4062 | 81 | 16.96 | 18.4
100 | 50 | 390.625 | 100 | 20 | 20
After reranging, update the transmitter, DCS scaling, totaliser factor, alarm settings and the data sheet. Large changes need a new orifice calculation to ISO 5167.
Prepared by |  |  | Checked by
Name: |  |  | Name:
Signature: |  |  | Signature:
Date: |  |  | Date: