## How to Use
HOW TO USE: DP LEVEL TRANSMITTER RANGE CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Choose the configuration: open tank or dry leg, or wet leg.
2. Enter the process density, and the minimum and maximum level measured from the HP (lower) tapping.
3. For a wet leg enter the distance between the tappings and the fill fluid density.
4. Enter how far the transmitter sits below the HP tap (0 if level with it).
5. Use LRV and URV to range the transmitter; apply the DP values in the table during calibration.
What the formulas do
• DP = ρ<sub>p</sub> g (h + x) − ρ<sub>s</sub> g (H<sub>s</sub> + x) for a wet leg; the second term is 0 for an open tank or dry leg.
• LRV at minimum level, URV at maximum level; span = URV − LRV.
• Positive LRV is zero suppression, negative LRV is zero elevation.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Hydrostatic pressure P = ρ g h with standard gravity 9.80665 m/s². Heights measured from the HP tapping.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
DP LEVEL TRANSMITTER RANGE CALCULATOR
Project: Condensate drum LT 4201 |  |  |  | Calc no: CALC LT 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Installation
Configuration |  | Wet leg |  | Process liquid density (kg/m³) |  | 1000
Minimum level above HP tap (m) |  | 0 |  | Maximum level above HP tap (m) |  | 3
Distance between taps, wet leg height (m) |  | 3.5 |  | Wet leg fill density (kg/m³) |  | 1000
Transmitter below HP tap (m) |  | 0.5 |  | Output unit |  | mbar
Result
LRV (mbar) |  | -343.2328 |  | URV (mbar) |  | -49.0333
Span (mbar) |  | 294.1995 |  | Zero condition |  | Zero elevation
Calibration points
Level (%) | Level above HP tap (m) |  | Applied DP (mbar) |  | Output (mA) | Reading
0 | 0 |  | -343.2328 |  | 4
25 | 0.75 |  | -269.6829 |  | 8
50 | 1.5 |  | -196.133 |  | 12
75 | 2.25 |  | -122.5831 |  | 16
100 | 3 |  | -49.0333 |  | 20
Wet leg: the LP impulse line is filled with liquid of density ρs from the upper tap down to the transmitter. Open tank or dry leg: the LP side sees only gas or atmosphere (its head is neglected).
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: