## How to Use
HOW TO USE: CONTROL VALVE SIZING CALCULATOR (GAS AND VAPOUR)
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter gas molecular weight, specific heat ratio and compressibility at inlet conditions.
2. Enter xT from the valve manufacturer (globe valves about 0.7, ball and butterfly lower).
3. Fill mass flow, inlet and outlet pressure (absolute) and temperature for the three cases.
4. Read Y, Kv and Cv. CHOKED means the outlet pressure no longer affects flow.
5. Enter the rated Cv of your valve and check the Cv ratios.
What the formulas do
• ρ1 = P1 × M ÷ (Z × R × T1).
• x = (P1 − P2) ÷ P1; sizing x = smaller of x and Fγ × xT.
• Y = 1 − x ÷ (3 Fγ xT).
• Kv = W ÷ (27.3 Y √(x P1 ρ1)); Cv = 1.156 Kv.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: IEC 60534-2-1 compressible flow equations with mass flow: Kv = W ÷ (27.3 × Y × √(x × P1 × ρ1)), Fγ = γ ÷ 1.4, choked at x = Fγ × xT (pipe geometry factor FP taken as 1).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
CONTROL VALVE SIZING CALCULATOR (GAS AND VAPOUR)
Project: Fuel gas to burner FV 1201 | [5 empty] | Calc no: CALC CV 002 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Gas and valve data
Molecular weight (kg/kmol) |  |  | 18 |  |  | Specific heat ratio γ |  |  | 1.3
Compressibility Z |  |  | 0.98 |  |  | Pressure drop ratio factor xT |  |  | 0.72
Rated Cv of selected valve |  |  | 46 |  |  | Selected valve |  |  | Globe, 2", equal %
Fγ (calculated) |  |  | 0.92857 |  |  | Choked x = Fγ × xT |  |  | 0.66857
Sizing cases (pressures in bar a)
Case | Mass flow W (kg/h) | Inlet P1 | Outlet P2 | T1 (°C) | ρ1 (kg/m³) | x = ΔP ÷ P1 | Sizing x | Y | Required Kv | Required Cv | Cv ratio / regime
Minimum | 400 | 10 | 8.5 | 40 | 7.0544 | 0.15 | 0.15 | 0.92521 | 4.8683 | 5.6278 | 0.12 OK
Normal | 1000 | 10 | 8 | 40 | 7.0544 | 0.2 | 0.2 | 0.90028 | 10.8321 | 12.5219 | 0.27 OK
Maximum | 1500 | 9.5 | 7 | 40 | 6.7017 | 0.26316 | 0.26316 | 0.8688 | 15.4507 | 17.861 | 0.39 OK
Cv ratio at maximum flow (target ≤ 0.85) | [9 empty] | OK
Cv ratio at minimum flow (target ≥ 0.1) | [9 empty] | OK
Kv = W ÷ (27.3 × Y × √(x × P1 × ρ1)) with W in kg/h, P1 in bar a and ρ1 in kg/m³. Y = 1 − x ÷ (3 × Fγ × xT). Flow is choked when x ≥ Fγ × xT; then x is limited to that value. Check noise separately for high pressure drops.
Prepared by | [5 empty] | Checked by
Name: | [5 empty] | Name:
Signature: | [5 empty] | Signature:
Date: | [5 empty] | Date: