## How to Use
HOW TO USE: GAS FLOW CONVERSION: ACTUAL TO NM³/H, SM³/H AND SCFM
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter actual flow, line pressure (gauge), temperature and Z for each line.
2. Adjust atmospheric pressure for site altitude if needed.
3. Read Nm³/h, Sm³/h, SCFM and ACFM.
What the formulas do
• Nm³/h = Q × (P + Patm) ÷ 1.01325 × 273.15 ÷ T(K) ÷ Z.
• Sm³/h = Nm³/h × 288.15 ÷ 273.15.
• SCFM = Nm³/h × 288.706 ÷ 273.15 × 0.588578.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Ideal gas relation with compressibility: Q_ref = Q × (P_abs ÷ P_ref) × (T_ref ÷ T) × (Z_ref ÷ Z), Z_ref taken as 1. Normal 0 °C, 1.01325 bar a; standard 15 °C, 1.01325 bar a; US standard 60 °F, 14.696 psia.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
GAS FLOW CONVERSION: ACTUAL TO NM³/H, SM³/H AND SCFM
Project: Gas flow units |  |  |  |  | Calc no: CALC FT 004 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Reference data
Atmospheric pressure (bar a) |  | 1.0132 |  |  | Reference Z |  | Taken as 1 at reference conditions
Conversions
Line | Actual flow (m³/h) | Pressure (bar g) | Temp. (°C) | Z | Nm³/h (0 °C) | Sm³/h (15 °C) | SCFM (60 °F) | ACFM | Remarks
Compressor discharge | 500 | 6 | 40 | 1 | 3018.7107 | 3184.4829 | 1877.9306 | 294.289
Fuel gas header | 1200 | 3.5 | 25 | 0.99 | 4946.3543 | 5217.9828 | 3077.1116 | 706.2936
Nitrogen line | 80 | 8 | 20 | 1 | 663.0803 | 699.4932 | 412.5002 | 47.0862
Always state which reference conditions are used. Nm³ and Sm³ differ by about 5.5 %. 1 m³/h = 0.588578 ft³/min.
Prepared by |  |  |  |  | Checked by
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: