## How to Use
HOW TO USE: INSTRUMENT AIR CONSUMPTION AND RECEIVER SIZING
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. List each type of air user with quantity, steady consumption and air used per stroke from the vendor data.
2. Estimate strokes per hour for modulating valves (positioner activity) and on off valves.
3. Set leakage and margin allowances from your project specification.
4. Enter the receiver pressure, minimum header pressure and the required hold up time.
5. Use the total with margin to size compressors and dryers, and the receiver volume for the storage vessel.
What the formulas do
• Steady total = qty × steady consumption.
• Stroking total = qty × air per stroke × strokes per hour ÷ 1000.
• Design demand = total × (1 + leakage) × (1 + margin).
• Receiver volume = hold time × demand with leakage ÷ 60 × Pa ÷ (P1 − P2).
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Free air (Nm³/h) totals with design margin; receiver volume V = t × (C − S) × Pa ÷ (P1 − P2), the drawdown method used in compressed air system guides.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
INSTRUMENT AIR CONSUMPTION AND RECEIVER SIZING
Project: Boiler 3 instrument air |  |  |  |  | Calc no: CALC IA 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Design data
Leakage allowance (%) |  | 10 |  |  | Design margin (%) |  | 20
Hold up time after compressor trip (min) |  | 10 |  |  | Receiver normal pressure (bar g) |  | 7
Minimum header pressure (bar g) |  | 4.5 |  |  | Atmospheric pressure (bar a) |  | 1.013
Air users
User | Qty | Steady each (Nm³/h) | Air per stroke each (L free) | Strokes per hour each | Steady total (Nm³/h) | Stroking total (Nm³/h) | Total (Nm³/h) | Remarks
Control valve positioners (digital) | 18 | 0.1 | 6 | 20 | 1.8 | 2.16 | 3.96
On off valve actuators | 10 | 0 | 25 | 2 | 0 | 0.5 | 0.5
I/P converters | 4 | 0.25 |  |  | 1 | 0 | 1
Analyser shelter purge | 1 | 6 |  |  | 6 | 0 | 6
Gas analyser (sample aspirator) | 2 | 1.2 |  |  | 2.4 | 0 | 2.4
Total connected demand (Nm³/h) | [7 empty] | 13.86
With leakage and margin (Nm³/h) | [7 empty] | 18.2952
Required receiver volume (m³) | [7 empty] | 1.0296
Receiver volume V = t × C × Pa ÷ (P1 − P2), with t the hold up time in minutes, C the demand with leakage in Nm³/min (no compressor supply during the event) and P1 − P2 the usable pressure band. Design margin applies to compressor sizing, not to the hold up volume.
Prepared by |  |  |  |  | Checked by
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: