## How to Use
HOW TO USE: 4 TO 20 MA LOOP POWER BUDGET CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the supply voltage and the transmitter minimum operating voltage from its data sheet.
2. Enter the maximum loop current (use the upscale alarm current).
3. Add the receiver input resistance, any barrier or isolator resistance and other series items.
4. Enter cable length and conductor size; the cable resistance is calculated for both cores.
5. Check the margin, maximum cable length and HART resistance.
What the formulas do
• Cable resistance = 2 × length × R/km × (1 + 0.00393 (T − 20)).
• V<sub>tx</sub> = V<sub>s</sub> − I<sub>max</sub> × R<sub>total</sub>; margin = V<sub>tx</sub> − V<sub>min</sub>.
• R<sub>max</sub> = (V<sub>s</sub> − V<sub>min</sub>) ÷ I<sub>max</sub>.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Ohm's law; copper conductor resistance from IEC 60228 class 2 at 20 °C with temperature correction.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
4 TO 20 MA LOOP POWER BUDGET CALCULATOR
Project: PT 1101 loop |  | Calc no: CALC LP 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Loop data
Supply voltage (V DC) | 24 | Transmitter minimum voltage (V) | 10.5
Maximum loop current (mA) | 22 | Receiver / AI input resistance (Ω) | 250
Barrier or isolator resistance (Ω) | 0 | Other series resistance (Ω) | 0
Cable length, one way (m) | 800 | Conductor size (mm²) | 1.5
Conductor temperature (°C) | 40
Result
Conductor resistance at 20 °C (Ω/km) | 12.1 | Loop cable resistance, both cores (Ω) | 20.8817
Total loop resistance (Ω) | 270.8817 | Voltage at transmitter at max current (V) | 18.0406
Margin above minimum (V) | 7.5406 | Loop power check | OK
Maximum allowed loop resistance (Ω) | 613.6364 | Maximum cable length, one way (m) | 13931.2961
HART resistance (≥ 230 Ω) | OK
Use the maximum current the transmitter can drive (alarm or saturation current, typically 21 to 23 mA) and the minimum supply voltage, including tolerance and any drop in the power supply distribution.
Prepared by |  | Checked by
Name: |  | Name:
Signature: |  | Signature:
Date: |  | Date: