## How to Use
HOW TO USE: ORIFICE PLATE FLOW CALCULATOR (ISO 5167-2)
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the measured pipe inside diameter and the orifice bore at operating temperature.
2. Enter the DP in mbar and the liquid density and viscosity at flowing conditions.
3. Choose the tapping arrangement; L1 and L2' follow automatically.
4. The iteration table refines C and Re; the last row gives the result.
5. Check that the ISO 5167-2 limits row shows OK.
What the formulas do
• β = d ÷ D, E = 1 ÷ √(1 − β⁴).
• C from the Reader Harris/Gallagher equation (ISO 5167-2).
• q<sub>m</sub> = C × E × (π ÷ 4) × d² × √(2 × ΔP × ρ).
• Re = 4 q<sub>m</sub> ÷ (π μ D), fed back into C until it converges.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: ISO 5167-2:2003 Reader Harris/Gallagher equation for C and permanent pressure loss; liquid service (ε = 1).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
ORIFICE PLATE FLOW CALCULATOR (ISO 5167-2)
Project: Feed flow FE 3101 |  |  |  | Calc no: CALC FE 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Inputs
Pipe inside diameter D (mm) |  | 102.26 |  | Orifice bore d (mm) | 63
Differential pressure (mbar) |  | 250 |  | Density ρ (kg/m³) | 998.2
Viscosity μ (cP = mPa·s) |  | 1.002 |  | Pressure tappings | Flange
Geometry (calculated)
Beta ratio β = d ÷ D |  | 0.61608 |  | Velocity of approach factor E | 1.0809
L1 (upstream tap ÷ D) |  | 0.24839 |  | L2' (downstream tap ÷ D) | 0.24839
M2' = 2 L2' ÷ (1 − β) |  | 1.2939
Iteration of discharge coefficient C and Reynolds number
Iteration | Re (assumed) |  | Discharge coefficient C | Mass flow (kg/s) | Re (calculated)
1 | 1000000 |  | 0.60626 | 14.4311 | 179323.2874
2 | 179323.2874 |  | 0.60959 | 14.5105 | 180309.4508
3 | 180309.4508 |  | 0.60958 | 14.5101 | 180304.928
4 | 180304.928 |  | 0.60958 | 14.5101 | 180304.9486
5 | 180304.9486 |  | 0.60958 | 14.5101 | 180304.9485
6 | 180304.9485 |  | 0.60958 | 14.5101 | 180304.9485
7 | 180304.9485 |  | 0.60958 | 14.5101 | 180304.9485
8 | 180304.9485 |  | 0.60958 | 14.5101 | 180304.9485
Discharge coefficient C | [5 empty] | 0.60958
Mass flow (kg/h) | [5 empty] | 52236.436
Volume flow (m³/h) | [5 empty] | 52.3306
Pipe Reynolds number | [5 empty] | 180304.9485
Pipe velocity (m/s) | [5 empty] | 1.7699
Permanent pressure loss (mbar) | [5 empty] | 152.3798
ISO 5167-2 limits (β 0.1 to 0.75, D 50 to 1000 mm, d ≥ 12.5 mm, Re) | [5 empty] | OK
For gas or steam add the expansibility factor ε; this sheet assumes an incompressible liquid. Iteration converges within a few steps for normal conditions.
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: