## How to Use
HOW TO USE: PID TUNING CALCULATOR (STEP TEST AND ULTIMATE GAIN)
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Make a step change of the controller output in manual and record the PV response.
2. Estimate the process gain K, dead time θ and time constant τ from the curve (tangent or 28 % / 63 % method).
3. Enter them, choose λ for lambda and IMC tuning, and optionally Ku and Pu from a closed loop test.
4. Pick the method that suits the loop, apply the settings and fine tune on the process.
What the formulas do
• Gains and times from the standard rules for each method.
• Proportional band = 100 ÷ Kc; reset rate = 1 ÷ Ti.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Published tuning rules (Ziegler–Nichols 1942, Cohen–Coon 1953, lambda and IMC) for a first order plus dead time model, ideal PID form.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
PID TUNING CALCULATOR (STEP TEST AND ULTIMATE GAIN)
Project: TIC 2101 reactor temperature |  |  |  | Calc no: CALC TUNE 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Step test (first order plus dead time)
Process gain K (% PV ÷ % output) |  | 1.5 |  | Time constant τ (min) |  | 4
Dead time θ (min) |  | 1 |  | Lambda λ (min) |  | 4
Ultimate gain test (optional)
Ultimate gain Ku |  | 4 |  | Ultimate period Pu (min) |  | 2
Controller settings (ideal form, times in minutes)
Method | Gain Kc | Proportional band (%) | Ti (min) | Reset (repeats/min) | Td (min)
ZN open loop P | 2.6667 | 37.5
ZN open loop PI | 2.4 | 41.6667 | 3.33 | 0.3003
ZN open loop PID | 3.2 | 31.25 | 2 | 0.5 | 0.5
Cohen–Coon PI | 2.4556 | 40.724 | 2.1964 | 0.45528
Cohen–Coon PID | 3.7222 | 26.8657 | 2.2333 | 0.44776 | 0.34783
Lambda PI | 0.53333 | 187.5 | 4 | 0.25
IMC PID | 0.66667 | 150 | 4.5 | 0.22222 | 0.44444
ZN closed loop PI | 1.8 | 55.5556 | 1.6667 | 0.6
ZN closed loop PID | 2.4 | 41.6667 | 1 | 1 | 0.25
Ziegler–Nichols and Cohen–Coon give fast, oscillatory responses (quarter decay). Lambda and IMC give smooth, robust loops; choose λ between τ and 3τ, and at least 3θ. Convert to your controller's form (series or parallel) if it is not ideal.
Tuned by |  |  |  | Approved by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: