## How to Use
HOW TO USE: INSULATED PIPE HEAT LOSS CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter surface coefficient and hours.
2. For each line enter OD, insulation thickness and conductivity, temperatures and length.
3. Read loss per metre, surface temperature, total and annual energy.
4. Compare with bare pipe to see the insulation saving.
What the formulas do
• Q/L = ΔT ÷ [ln(r2/r1)/(2πk) + 1/(2π r2 h)].
• Surface T = Ta + (Q/L) ÷ (2π r2 h).
• Energy = kW × hours ÷ 1000 (MWh/yr).
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Steady state radial conduction plus outer film: Q/L = (Ti − Ta) ÷ [ln(r2/r1) ÷ (2πk) + 1 ÷ (2π r2 h)]. Pipe wall and inner film resistance neglected.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
INSULATED PIPE HEAT LOSS CALCULATOR
Project: Utility line heat loss | [5 empty] | Calc no: CALC TH 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Common data
Outer surface coefficient h (W/m²K) |  |  | 10 |  |  | Operating hours per year |  |  | 8000
Lines
Line | Pipe OD (mm) | Insulation (mm) | k (W/mK) | Fluid T (°C) | Ambient (°C) | Length (m) | Loss (W/m) | Surface T (°C) | Line loss (kW) | Energy (MWh/yr) | Bare pipe (W/m) | Remarks
Steam 4" | 114.3 | 50 | 0.04 | 180 | 25 | 50 | 58.5026 | 33.6897 | 2.9251 | 23.401 | 556.5803
Condensate 2" | 60.3 | 40 | 0.04 | 120 | 25 | 30 | 26.4857 | 31.009 | 0.79457 | 6.3566 | 179.9661
Hot oil 3" | 88.9 | 75 | 0.045 | 250 | 25 | 40 | 61.9927 | 33.2599 | 2.4797 | 19.8377 | 628.3971
Total loss (kW) | [10 empty] | 6.1994
Total energy (MWh/yr) | [10 empty] | 49.5953
h about 10 W/m²K suits still air indoors; use higher values for wind. Bare pipe loss uses the same h and ignores radiation, so it is a low estimate.
Prepared by | [5 empty] | Checked by
Name: | [5 empty] | Name:
Signature: | [5 empty] | Signature:
Date: | [5 empty] | Date: