## How to Use
HOW TO USE: PIPE VELOCITY AND LINE SIZING CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the flow rate and the minimum and maximum acceptable velocity for the service.
2. Read the velocity in each Schedule 40 size.
3. The smallest size within the limits is selected automatically; also check pressure drop for long lines.
What the formulas do
• A = π ÷ 4 × ID².
• v = Q (m³/h) ÷ 3600 ÷ A.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Schedule 40 inside diameters from ASME B36.10M wall thickness. Velocity v = Q ÷ A.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
PIPE VELOCITY AND LINE SIZING CALCULATOR
Project: Cooling water return |  |  | Calc no: CALC PS 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Flow
Flow rate (m³/h) |  | 60 | Maximum velocity (m/s) |  | 3
Service |  | Water, pump discharge | Minimum velocity (m/s) |  | 0.5
Velocity in each line size (Schedule 40)
NPS | DN | Inside diameter (mm) | Area (m²) | Velocity (m/s) | Within limits
1/2" | 15 | 15.8 | 0.00019607 | 85.005 | CHECK
3/4" | 20 | 20.93 | 0.00034406 | 48.4418 | CHECK
1" | 25 | 26.64 | 0.00055739 | 29.9013 | CHECK
1 1/2" | 40 | 40.89 | 0.0013132 | 12.6918 | CHECK
2" | 50 | 52.5 | 0.0021648 | 7.6991 | CHECK
3" | 80 | 77.92 | 0.0047686 | 3.4951 | CHECK
4" | 100 | 102.26 | 0.008213 | 2.0293 | OK
6" | 150 | 154.05 | 0.018639 | 0.8942 | OK
8" | 200 | 202.72 | 0.032276 | 0.51638 | OK
10" | 250 | 254.51 | 0.050874 | 0.3276 | CHECK
12" | 300 | 303.23 | 0.072216 | 0.23079 | CHECK
Smallest size within the velocity limits |  |  |  |  | 4"
Velocity in that size (m/s) |  |  |  |  | 2.0293
Typical velocities: water pump discharge 1.5 to 3 m/s, suction 0.6 to 1.5 m/s, saturated steam 20 to 35 m/s, compressed air 6 to 10 m/s. Magnetic flowmeters measure best at 1 to 3 m/s.
Prepared by |  |  | Checked by
Name: |  |  | Name:
Signature: |  |  | Signature:
Date: |  |  | Date: