## How to Use
HOW TO USE: PLC I/O COUNT AND MODULE CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Set spare % and channels per module for your PLC family.
2. List device types with their AI, AO, DI and DO per device.
3. Enter quantities from the instrument index and motor list.
4. Read totals, totals with spare and modules required.
5. Transfer to the IO list template for detailed allocation.
What the formulas do
• Total = Σ quantity × points.
• With spare = ROUNDUP(total × (1 + spare)).
• Modules = ROUNDUP(with spare ÷ channels).
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Totals = Σ quantity × points per device. Modules = ROUNDUP(total × (1 + spare) ÷ channels per module).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
PLC I/O COUNT AND MODULE CALCULATOR
Project: Boiler 3 PLC |  |  |  | Calc no: CALC PLC 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Design data
Spare (%) |  | 20 |  | AI channels per module |  | 8
AO channels per module |  | 8 |  | DI channels per module |  | 16
DO channels per module |  | 16
Device types
Device type | Signals | AI each | AO each | DI each | DO each | Quantity | Total points | Remarks
Pressure transmitter | AI | 1 | 0 | 0 | 0 | 24 | 24
Temperature transmitter | AI | 1 | 0 | 0 | 0 | 18 | 18
Control valve | AO | 0 | 1 | 0 | 0 | 12 | 12
On off valve (2 limit switches + solenoid) | DI/DO | 0 | 0 | 2 | 1 | 10 | 30
Motor (run, trip, start, stop) | DI/DO | 0 | 0 | 2 | 2 | 8 | 32
Level switch | DI | 0 | 0 | 1 | 0 | 6 | 6
AI total / with spare / modules | [6 empty] | 42 / 51 / 7
AO total / with spare / modules | [6 empty] | 12 / 15 / 2
DI total / with spare / modules | [6 empty] | 42 / 51 / 4
DO total / with spare / modules | [6 empty] | 26 / 32 / 2
Total points | [6 empty] | 122
Points per device depend on your typicals; edit them to match. Safety and redundant I/O may need separate modules. Group by marshalling and cabinet later in the IO list.
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: