## How to Use
HOW TO USE: POWER FACTOR CORRECTION CAPACITOR CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the load power in kW, the existing and target power factor, voltage and frequency.
2. Choose star or delta for the capacitor bank.
3. Read the kVAR rating, current reduction and capacitance per phase.
4. Use the table to compare the cost of different target power factors.
What the formulas do
• Qc = P × (tan(acos PF1) − tan(acos PF2)).
• I = P ÷ (√3 × V × PF).
• Delta: C per phase = Qc ÷ 3 ÷ (2πf V²); Star: C per phase = Qc ÷ (2πf V²).
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Power triangle: Qc = P × (tan φ1 − tan φ2); capacitance from Q = V² × 2πfC.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
POWER FACTOR CORRECTION CAPACITOR CALCULATOR
Project: MCC 2 capacitor bank |  |  |  | Calc no: CALC PF 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Load
Active power P (kW) |  | 100 |  | Existing power factor |  | 0.8
Target power factor |  | 0.95 |  | Line voltage (V) |  | 415
Frequency (Hz) |  | 50 |  | Bank connection |  | Delta
Result
Capacitor rating (kVAR) |  | 42.1316 |  | kVA before |  | 125
kVA after |  | 105.2632 |  | Line current before (A) |  | 173.9007
Line current after (A) |  | 146.4427 |  | Capacitor line current (A) |  | 58.6137
Capacitance per phase (µF) |  | 259.5616
kVAR for other target power factors
Target PF | kVAR needed |  | Line current (A) |  | kVA
0.85 | 13.0256 |  | 163.6712 |  | 117.6471
0.9 | 26.5678 |  | 154.5784 |  | 111.1111
0.92 | 32.4002 |  | 151.218 |  | 108.6957
0.95 | 42.1316 |  | 146.4427 |  | 105.2632
0.97 | 49.9376 |  | 143.4232 |  | 103.0928
0.98 | 54.6941 |  | 141.9597 |  | 102.0408
0.99 | 60.7508 |  | 140.5258 |  | 101.0101
1 | 75 |  | 139.1205 |  | 100
Avoid over correction (leading PF) at light load: use an automatic stepped bank. Where VFDs or other harmonic sources are present, use detuned capacitors with series reactors.
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: