## How to Use
HOW TO USE: PT100 AND PT1000 RESISTANCE TABLE GENERATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter R0: 100 for Pt100 or 1000 for Pt1000.
2. Read resistance, tolerances and Ω bands at each temperature.
3. Enter a measured resistance to get the temperature (0 °C and above).
4. Print the table as a field reference.
What the formulas do
• R = R0 (1 + A t + B t²) for t ≥ 0 °C; add C (t − 100) t³ below 0 °C.
• Class A: ± (0.15 + 0.002 ¦t¦) °C; class B: ± (0.3 + 0.005 ¦t¦) °C.
• Inverse for t ≥ 0: t = (−A + √(A² − 4B (1 − R/R0))) ÷ 2B.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: IEC 60751 Callendar Van Dusen equation: R = R0 (1 + A t + B t² + C (t − 100) t³), C used below 0 °C only. A = 3.9083 × 10⁻³, B = −5.775 × 10⁻⁷, C = −4.183 × 10⁻¹².
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
PT100 AND PT1000 RESISTANCE TABLE GENERATOR
Project: RTD reference table |  |  |  | Calc no: CALC TE 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Sensor
R0 at 0 °C (100 for Pt100, 1000 for Pt1000) |  | 100 |  | Measured resistance for lookup (Ω) |  | 138.51
Temperature from measured R (°C, valid ≥ 0 °C) |  | 100.0119 |  | Sensitivity near 0 to 100 °C (Ω/°C) |  | 0.385
Resistance table
Temperature (°C) | Resistance (Ω) | Class A tolerance (± °C) | Class B tolerance (± °C) | Class A band (± Ω) | Class B band (± Ω) | R ÷ R0 | Notes
-50 | 80.3063 | 0.25 | 0.55 | 0.099151 | 0.21813 | 0.80306
-40 | 84.2707 | 0.23 | 0.5 | 0.090954 | 0.19773 | 0.84271
-30 | 88.2217 | 0.21 | 0.45 | 0.082802 | 0.17743 | 0.88222
-20 | 92.1599 | 0.19 | 0.4 | 0.074697 | 0.15726 | 0.9216
-10 | 96.0859 | 0.17 | 0.35 | 0.066637 | 0.13719 | 0.96086
0 | 100 | 0.15 | 0.3 | 0.058625 | 0.11725 | 1
10 | 103.9025 | 0.17 | 0.35 | 0.066245 | 0.13639 | 1.039
20 | 107.7935 | 0.19 | 0.4 | 0.073819 | 0.15541 | 1.0779
30 | 111.6729 | 0.21 | 0.45 | 0.081347 | 0.17431 | 1.1167
40 | 115.5408 | 0.23 | 0.5 | 0.088828 | 0.1931 | 1.1554
50 | 119.3971 | 0.25 | 0.55 | 0.096264 | 0.21178 | 1.194
60 | 123.2419 | 0.27 | 0.6 | 0.10365 | 0.23034 | 1.2324
70 | 127.0751 | 0.29 | 0.65 | 0.111 | 0.24878 | 1.2708
80 | 130.8968 | 0.31 | 0.7 | 0.11829 | 0.26711 | 1.309
90 | 134.7069 | 0.33 | 0.75 | 0.12554 | 0.28533 | 1.3471
100 | 138.5055 | 0.35 | 0.8 | 0.13275 | 0.30342 | 1.3851
110 | 142.2925 | 0.37 | 0.85 | 0.13991 | 0.32141 | 1.4229
120 | 146.068 | 0.39 | 0.9 | 0.14702 | 0.33927 | 1.4607
130 | 149.8319 | 0.41 | 0.95 | 0.15408 | 0.35702 | 1.4983
140 | 153.5843 | 0.43 | 1 | 0.1611 | 0.37466 | 1.5358
150 | 157.3251 | 0.45 | 1.05 | 0.16808 | 0.39218 | 1.5733
160 | 161.0544 | 0.47 | 1.1 | 0.175 | 0.40958 | 1.6105
170 | 164.7721 | 0.49 | 1.15 | 0.18189 | 0.42687 | 1.6477
180 | 168.4783 | 0.51 | 1.2 | 0.18872 | 0.44405 | 1.6848
190 | 172.1729 | 0.53 | 1.25 | 0.19551 | 0.46111 | 1.7217
200 | 175.856 | 0.55 | 1.3 | 0.20225 | 0.47805 | 1.7586
210 | 179.5275 | 0.57 | 1.35 | 0.20895 | 0.49488 | 1.7953
220 | 183.1875 | 0.59 | 1.4 | 0.2156 | 0.51159 | 1.8319
230 | 186.8359 | 0.61 | 1.45 | 0.2222 | 0.52818 | 1.8684
240 | 190.4728 | 0.63 | 1.5 | 0.22876 | 0.54466 | 1.9047
250 | 194.0981 | 0.65 | 1.55 | 0.23527 | 0.56103 | 1.941
260 | 197.7119 | 0.67 | 1.6 | 0.24174 | 0.57728 | 1.9771
270 | 201.3141 | 0.69 | 1.65 | 0.24816 | 0.59341 | 2.0131
280 | 204.9048 | 0.71 | 1.7 | 0.25453 | 0.60943 | 2.049
290 | 208.4839 | 0.73 | 1.75 | 0.26085 | 0.62534 | 2.0848
300 | 212.0515 | 0.75 | 1.8 | 0.26714 | 0.64112 | 2.1205
310 | 215.6075 | 0.77 | 1.85 | 0.27337 | 0.6568 | 2.1561
320 | 219.152 | 0.79 | 1.9 | 0.27956 | 0.67235 | 2.1915
330 | 222.6849 | 0.81 | 1.95 | 0.2857 | 0.68779 | 2.2268
340 | 226.2063 | 0.83 | 2 | 0.29179 | 0.70312 | 2.2621
350 | 229.7161 | 0.85 | 2.05 | 0.29784 | 0.71833 | 2.2972
360 | 233.2144 | 0.87 | 2.1 | 0.30385 | 0.73342 | 2.3321
370 | 236.7011 | 0.89 | 2.15 | 0.3098 | 0.7484 | 2.367
380 | 240.1763 | 0.91 | 2.2 | 0.31572 | 0.76327 | 2.4018
390 | 243.6399 | 0.93 | 2.25 | 0.32158 | 0.77802 | 2.4364
400 | 247.092 | 0.95 | 2.3 | 0.3274 | 0.79265 | 2.4709
Values follow IEC 60751. Class A applies from −100 to 450 °C for wire wound and −30 to 300 °C for thin film elements; class B over wider ranges. The lookup uses the quadratic inverse valid at or above 0 °C.
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: