## How to Use
HOW TO USE: SIL VERIFICATION (PFDAVG) CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the SIF and its target SIL from the safety requirements specification.
2. List each subsystem with its voting, λDU per channel in FIT (failures per 10⁹ h), proof test interval and β for redundant groups.
3. Read the PFDavg of each subsystem and its share of the total; the largest share is where improvement pays most.
4. Check the achieved SIL against the target.
5. Shorten test intervals, add redundancy or choose better devices if the target is not met.
What the formulas do
• λ = λDU (FIT) × 10⁻⁹ per hour; TI in hours = months × 730.
• 1oo1: λTI/2; 2oo2: λTI; 1oo2: (λTI)²/3 + βλTI/2; 2oo3: (λTI)² + βλTI/2.
• Total PFDavg = sum of subsystems; RRF = 1 ÷ PFDavg.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Simplified IEC 61508 / ISA TR84.00.02 PFDavg equations (no diagnostics or repair time): 1oo1 λTI/2, 2oo2 λTI, 1oo2 (λTI)²/3 + βλTI/2, 2oo3 (λTI)² + βλTI/2.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
SIL VERIFICATION (PFDAVG) CALCULATOR
Project: SIF 101: steam header high high pressure |  |  |  |  | Calc no: CALC SIL 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Safety function
SIF |  | SIF 101 |  |  | Target SIL |  | SIL 2
Demand mode |  | Low demand |  |  | SRS reference |  | SRS 101 rev A
Subsystems
Subsystem | Voting | λDU per channel (FIT) | Proof test interval (months) | β (%) | PFDavg | Share of total (%) |  | Remarks
Pressure transmitters PT 1101 A/B/C | 2oo3 | 150 | 12 | 5 | 3.4577e-05 | 1.9162
Safety PLC (from certificate) | 1oo1 | 20 | 120 |  | 0.000876 | 48.5474
Fuel gas SDVs XV 1101 / 1102 | 1oo2 | 1500 | 12 | 10 | 0.00071455 | 39.6001
Solenoid valves | 1oo2 | 400 | 12 | 10 | 0.00017929 | 9.9363
Total PFDavg | [7 empty] | 0.0018044
Risk reduction factor | [7 empty] | 554.1939
Achieved SIL (PFDavg band) | [7 empty] | SIL 2
Meets target? | [7 empty] | OK
PFDavg of the SIF = sum of subsystem PFDavg. SIL bands (low demand): SIL 1 10⁻² to 10⁻¹, SIL 2 10⁻³ to 10⁻², SIL 3 10⁻⁴ to 10⁻³. Architectural constraints (hardware fault tolerance) and systematic capability must also be met.
Prepared by |  |  |  |  | Verified by
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: