## How to Use
HOW TO USE: DP FLOW SQUARE ROOT SCALING TABLE
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the maximum flow, the DP at that flow and a low flow cut off.
2. Use the table for calibration and for checking DCS readings.
3. Type a measured DP into the live conversion to get the flow instantly.
4. Remember: take the square root in the transmitter or in the DCS, not both.
What the formulas do
• DP = DP<sub>max</sub> × (Q ÷ Q<sub>max</sub>)².
• Q = Q<sub>max</sub> × √(DP ÷ DP<sub>max</sub>).
• Linear DP output: mA = 4 + 16 × DP%; square root output: mA = 4 + 16 × flow%.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Square law of DP flow elements: Q ÷ Q<sub>max</sub> = √(ΔP ÷ ΔP<sub>max</sub>).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
DP FLOW SQUARE ROOT SCALING TABLE
Project: FT 3101 orifice flow |  |  |  | Calc no: CALC FT 002 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Range
Maximum flow |  | 120 |  | Flow unit |  | m³/h
DP at maximum flow (mbar) |  | 250 |  | Low flow cut off (% flow) |  | 6
Live conversion
Measured DP (mbar) |  | 62.5 |  | Flow at measured DP |  | 60
Flow (%) |  | 50 |  | mA (square root output) |  | 12
Flow, DP and output
Flow (%) | Flow | DP (mbar) | DP (%) | mA, linear DP output | mA, square root output | Cut off
0 | 0 | 0 | 0 | 4 | 4 | Below cut off
5 | 6 | 0.625 | 0.25 | 4.04 | 4.8 | Below cut off
10 | 12 | 2.5 | 1 | 4.16 | 5.6
15 | 18 | 5.625 | 2.25 | 4.36 | 6.4
20 | 24 | 10 | 4 | 4.64 | 7.2
25 | 30 | 15.625 | 6.25 | 5 | 8
30 | 36 | 22.5 | 9 | 5.44 | 8.8
35 | 42 | 30.625 | 12.25 | 5.96 | 9.6
40 | 48 | 40 | 16 | 6.56 | 10.4
45 | 54 | 50.625 | 20.25 | 7.24 | 11.2
50 | 60 | 62.5 | 25 | 8 | 12
55 | 66 | 75.625 | 30.25 | 8.84 | 12.8
60 | 72 | 90 | 36 | 9.76 | 13.6
65 | 78 | 105.625 | 42.25 | 10.76 | 14.4
70 | 84 | 122.5 | 49 | 11.84 | 15.2
75 | 90 | 140.625 | 56.25 | 13 | 16
80 | 96 | 160 | 64 | 14.24 | 16.8
85 | 102 | 180.625 | 72.25 | 15.56 | 17.6
90 | 108 | 202.5 | 81 | 16.96 | 18.4
95 | 114 | 225.625 | 90.25 | 18.44 | 19.2
100 | 120 | 250 | 100 | 20 | 20
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: