## How to Use
HOW TO USE: TRANSMITTER TOTAL PROBABLE ERROR CALCULATOR
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the transmitter URL and the calibrated span in the same unit.
2. List each error source with its value and whether it is in % of span, % of URL or engineering units.
3. Scale temperature and static pressure effects to your actual conditions before entering them.
4. Read the total probable error (RSS) and compare it with the accuracy the loop needs.
What the formulas do
• % URL values × URL ÷ span give % of span.
• TPE = √(Σ error²) in % of span.
• The simple sum shows the absolute worst case.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: Root sum square combination of independent errors, as used in manufacturer total performance calculations.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
TRANSMITTER TOTAL PROBABLE ERROR CALCULATOR
Project: FT 3101 DP flow loop |  |  |  | Calc no: CALC ACC 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Transmitter
Upper range limit URL |  | 250 |  | Calibrated span |  | 100
Unit |  | mbar |  | Model |  | Smart DP transmitter (example values)
Error sources (enter values from the data sheet for your conditions)
Error source | Value (±) | Basis | In % of span | Squared | In units
Reference accuracy | 0.065 | % span | 0.065 | 0.004225 | 0.065
Ambient temperature effect (URL part) | 0.025 | % URL | 0.0625 | 0.0039062 | 0.0625
Ambient temperature effect (span part) | 0.125 | % span | 0.125 | 0.015625 | 0.125
Static pressure effect | 0.1 | % URL | 0.25 | 0.0625 | 0.25
Long term stability | 0.125 | % URL | 0.3125 | 0.097656 | 0.3125
Power supply effect | 0.005 | % span | 0.005 | 2.5e-05 | 0.005
DCS analog input card | 0.1 | % span | 0.1 | 0.01 | 0.1
Total probable error, RSS (% of span) | [5 empty] | 0.44038
Total probable error (units) | [5 empty] | 0.44038
Worst case, simple sum (% of span) | [5 empty] | 0.92
Example values are typical of smart DP transmitters and are for illustration only. Temperature effects are usually stated per 28 °C (50 °F) change; scale them for your expected ambient range.
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: