## How to Use
HOW TO USE: UPS AND BATTERY SIZING FOR CONTROL SYSTEMS
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. List all loads fed by the UPS.
2. Set power factor, margin and backup time.
3. Enter battery voltage, inverter efficiency, ageing and depth of discharge.
4. Read UPS kVA and battery Ah.
5. Confirm with vendor discharge data.
What the formulas do
• kVA = ΣW ÷ PF × (1 + margin) ÷ 1000.
• Ah = ΣW × t ÷ (Vdc × η) × ageing ÷ DoD.
Sheet "Calculator" holds a worked example: overwrite the yellow cells with your own data.
Basis: UPS kVA = Σ W ÷ PF × (1 + margin). Battery Ah = P × t ÷ (Vdc × η) × ageing factor ÷ depth of discharge. Simplified constant power method; final sizing per battery maker discharge tables (for example IEEE 485 approach).
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Calculator
UPS AND BATTERY SIZING FOR CONTROL SYSTEMS
Project: DCS and SIS UPS |  |  |  | Calc no: CALC EL 003 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Design data
Load power factor |  | 0.9 |  | Design margin (%) |  | 25
Backup time (h) |  | 1 |  | Battery bank voltage (V DC) |  | 192
Inverter efficiency (0 to 1) |  | 0.9 |  | Ageing factor |  | 1.25
Usable depth of discharge (0 to 1) |  | 0.8
UPS loads
No | Load | Qty | Power each (W) | Total (W) | Critical? | Remarks
1 | DCS controller cabinets | 2 | 600 | 1200 | Yes
2 | SIS cabinet | 1 | 500 | 500 | Yes
3 | Operator stations | 3 | 350 | 1050 | Yes
4 | Network switches | 4 | 60 | 240 | Yes
5 | Field 24 V DC supplies | 2 | 480 | 960 | Yes
6
7
8
9
10
11
12
13
14
15
Total load (W) | [5 empty] | 3950
UPS rating with margin (kVA) | [5 empty] | 5.4861
Battery capacity required (Ah) | [5 empty] | 35.7169
Battery energy (kWh) | [5 empty] | 6.8576
Battery capacity depends strongly on discharge rate and temperature; check against the battery maker discharge tables. Size for end of life capacity (ageing factor).
Prepared by |  |  |  | Checked by
Name: |  |  |  | Name:
Signature: |  |  |  | Signature:
Date: |  |  |  | Date: