| Your Company Name / Logo | ANALYSER SHELTER ROUTINE INSPECTION SOP | Doc no: SOP ANA 003 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To keep analysers available and accurate and the shelter safe, by finding sample system and utility problems before they cause bad readings or hazards.

# 2. Scope

Analyser shelters, houses and cabinets with process gas or liquid analysers, sample conditioning systems and associated utilities.

# 3. References

- Analyser and sample system manuals

- Shelter ventilation and gas detection design basis

- Site entry and permit procedures

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Before entry, check the shelter gas detection status (flammable, toxic and oxygen) at the door panel. Do not enter on alarm.

- Keep the door closed during work so ventilation and purge stay effective.

# 6. Tools and equipment

- Portable multigas detector

- Inspection checklist

- Leak detection solution

- Torch and radio

# 7. Prerequisites

- Routine inspection permit or entry permission as required by the site.

- List of analysers in the shelter and their normal sample flows and pressures.

# 8. Procedure

## 8.1 Before entry

- Check the gas detection panel: no flammable, toxic or low oxygen alarms.

- Check the HVAC and purge status lights and the shelter differential pressure indicator.

## 8.2 Shelter and utilities

- Shelter temperature within the design range; HVAC running without alarms.

- Instrument air, nitrogen and carrier gas pressures normal; cylinder contents above the replacement level.

- Vent and drain headers clear; no liquid in drain pots above the normal level.

## 8.3 Sample systems

- Sample flows and pressures at their normal values for each analyser.

- Filters not blocked (check differential pressure or flow drop) and coalescer drains working.

- Heated lines and enclosures at the correct temperature; no condensation in gas samples.

- No leaks at fittings (check suspect joints with leak detection solution).

## 8.4 Analyser status

- Analysers in measure mode with no active faults; reading reasonable for the process.

- Last automatic validation or calibration passed; schedule the next one if due.

- Note any reading that disagrees with laboratory results for follow up.

## 8.5 Close out

- Record findings on the checklist, raise work orders for defects and inform the control room of any analyser out of service.

# 9. Acceptance criteria

- No gas detection alarms and correct shelter ventilation or purge.

- All analysers in service with sample flows and utilities within normal ranges, or defects reported.

- Inspection recorded with work orders for every defect.

# 10. Records

- Instrument PM schedule (free template: instrumentationblog.in/downloads/templates/instrument-preventive-maintenance-schedule/)

- Breakdown report (free template: instrumentationblog.in/downloads/templates/instrument-breakdown-report/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.