| Your Company Name / Logo | INSTRUMENT CABLE INSULATION RESISTANCE TEST SOP | Doc no: SOP INST 016 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To find damaged or wet cables before energising and during fault finding, without damaging electronics.

# 2. Scope

Low voltage instrument, control and thermocouple extension cables.

# 3. References

- Cable schedule

- Project test specification (test voltage and minimum IR)

- Insulation tester manual

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Insulation testers produce high voltage: warn others and do not touch cores during the test.

- In hazardous areas, megger testing needs a gas free certificate; IS circuits need special care.

- Discharge every core to earth after testing.

# 6. Tools and equipment

- Calibrated insulation tester

- Shorting links

- Multimeter

- Cable schedule and test record

# 7. Prerequisites

- Both ends disconnected from instruments, cards and barriers.

- Cable identified at both ends.

# 8. Procedure

## 8.1 Prepare

- Isolate and disconnect the cable at both ends; confirm no voltage with a multimeter.

- Record cable tag, cores and length.

## 8.2 Test

- Test core to core, core to earth and core to screen at the specified voltage (commonly 500 V DC).

- Hold the test about 1 minute and record the reading.

## 8.3 Discharge and restore

- Discharge each core to earth.

- Reconnect and check terminations and screens.

## 8.4 Record

- Record results and mark failures for repair and retest.

# 9. Acceptance criteria

- All readings at or above the minimum IR in the specification.

- Cores discharged and reconnected correctly.

# 10. Records

- Insulation resistance test record (free template: instrumentationblog.in/downloads/templates/cable-insulation-resistance-test-record/)

- Cable continuity test record (free template: instrumentationblog.in/downloads/templates/cable-continuity-test-record/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.