| Your Company Name / Logo | COLD LOOP CHECK SOP (CONTINUITY AND INSULATION) | Doc no: SOP COM 002 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To find wiring faults before energising instrument loops.

# 2. Scope

Instrument signal and power cables from field devices through junction boxes to marshalling cabinets.

# 3. References

- Loop drawings and termination schedules

- Cable schedule

- Insulation tester manual

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Insulation testers produce high voltage: make sure no one touches the circuit, and discharge cables after each test.

- Disconnect transmitters, I/O cards, barriers and surge protectors before testing; the test voltage can damage electronics.

- Do not use an insulation tester on IS circuits in a hazardous area without a gas free certificate.

# 6. Tools and equipment

- Insulation resistance tester (500 V DC for instrument cables)

- Multimeter or continuity tester

- Radios

- Termination schedules

# 7. Prerequisites

- Cables installed, glanded and terminated; ferrules fitted.

- Electronic devices at both ends disconnected.

# 8. Procedure

## 8.1 Continuity and polarity

- Short the pair at the field end.

- Measure continuity at the marshalling end and confirm the loop resistance is reasonable for the length.

- Remove the short and confirm open circuit; check polarity follows the drawings.

## 8.2 Insulation resistance

- Test core to core, each core to screen and each core to earth at 500 V DC for one minute.

- Record the readings; discharge the cable after each test.

## 8.3 Screen and earthing

- Confirm the screen is continuous through the junction box and earthed at one end only (normally the control room).

- Confirm the screen is isolated from earth at the field end.

## 8.4 Completion

- Reconnect devices, record results and raise punch items for failures.

# 9. Acceptance criteria

- Continuity and polarity as per drawings.

- Insulation resistance at or above the project requirement (commonly ≥ 100 MΩ for new instrument cables).

- Screen earthed at one point only.

# 10. Records

- Loop check sheet (pre checks) (free template: instrumentationblog.in/downloads/templates/loop-check-sheet/)

- Cable schedule (free template: instrumentationblog.in/downloads/templates/cable-schedule-template/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.