| Your Company Name / Logo | CONDUCTIVITY ANALYSER CALIBRATION SOP | Doc no: SOP ANA 004 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To keep conductivity readings accurate for water quality, blowdown and concentration control.

# 2. Scope

Contacting and inductive conductivity sensors with online transmitters.

# 3. References

- Analyser manual

- Standard solution certificate

- Site water chemistry limits

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Wear chemical gloves and eye protection when removing sensors from chemical lines.

# 6. Tools and equipment

- Certified conductivity standard near the normal reading

- Clean beakers and rinse water

- Reference thermometer

- Cleaning solution as the manufacturer advises

# 7. Prerequisites

- Loop in manual or alarms inhibited as authorised.

# 8. Procedure

## 8.1 Remove and clean

- Remove the sensor, rinse and clean deposits.

- Inspect electrodes or toroid for damage.

## 8.2 Calibrate

- Immerse in the standard at stable temperature without air bubbles.

- Check the temperature reading against the reference thermometer.

- Run the calibration so the analyser adjusts the cell constant to the standard value.

## 8.3 Verify

- Rinse, then check a second standard if available.

- Record cell constant, temperature coefficient and readings.

## 8.4 Return to service

- Reinstall the sensor, confirm a sensible process reading and remove inhibits.

# 9. Acceptance criteria

- Reading within tolerance of the standard (for example ± 2 % of reading).

- Cell constant change within the manufacturer limit.

- Temperature reading within ± 0.5 °C of reference.

# 10. Records

- Calibration master list (free template: instrumentationblog.in/downloads/templates/calibration-master-list/)

- Analyser datasheet (free template: instrumentationblog.in/downloads/templates/analyser-datasheet/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.