| Your Company Name / Logo | CONTROL VALVE STROKE TEST SOP | Doc no: SOP INST 007 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To confirm that a control valve follows its signal accurately across the full stroke and fails to the correct position.

# 2. Scope

Pneumatically actuated control valves with analog or digital positioners.

# 3. References

- Valve and positioner manuals

- Control valve data sheet (travel, fail action)

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Stroking a valve changes the process: do it only with the process isolated or with operations agreement and bypass in use.

- Keep hands clear of the yoke and stem connector; actuators move with great force.

# 6. Tools and equipment

- mA source or DCS output in manual

- Ruler or dial gauge for stem travel

- Stopwatch

- HART communicator or positioner software

# 7. Prerequisites

- Process isolated or bypassed; permit approved.

- Air supply pressure correct and regulator set to the actuator rating.

# 8. Procedure

## 8.1 Stroke check (as found)

- Apply 0, 25, 50, 75, 100 % signal and back down, recording travel at each point.

- Calculate position error in % of travel.

## 8.2 Positioner calibration

- If errors exceed tolerance, run the positioner auto calibration (travel calibration) or adjust zero and span.

- Repeat the stroke check (as left).

## 8.3 Stroke time and fail action

- Time full open and full close strokes.

- Remove the air supply (or signal, depending on design) and confirm the valve moves to its fail position.

- Check feedback and limit switches in the control system.

## 8.4 Return to service

- Restore air and signal, hand over to operations and close the permit.

# 9. Acceptance criteria

- Position error within tolerance at all points (typically ± 1 % of travel).

- Valve moves to the correct fail position.

- Feedback correct in the control system.

# 10. Records

- Control valve calibration report (free template: instrumentationblog.in/downloads/templates/control-valve-calibration-report/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.