| Your Company Name / Logo | DISSOLVED OXYGEN ANALYSER CALIBRATION SOP | Doc no: SOP ANA 005 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To keep DO readings accurate for aeration control and boiler water monitoring.

# 2. Scope

Optical (luminescent) and galvanic or polarographic DO sensors with online transmitters.

# 3. References

- Analyser manual

- Local barometric pressure

- Site DO control limits

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Wastewater basins: use fall protection and avoid contact with wastewater.

# 6. Tools and equipment

- Calibration sleeve or bottle with damp sponge

- Barometer or site pressure value

- Zero oxygen solution for zero check if required

- Soft brush and clean water

# 7. Prerequisites

- Aeration control in manual or a fixed blower setting agreed with operations.

# 8. Procedure

## 8.1 Clean and inspect

- Remove the sensor, clean the cap or membrane gently.

- Replace the sensor cap or membrane if damaged or due.

## 8.2 Air calibration

- Place the sensor in water saturated air in the calibration sleeve and let temperature stabilise.

- Enter barometric pressure if not measured automatically.

- Start the air calibration (100 % saturation).

## 8.3 Zero check (if required)

- Immerse in zero oxygen solution and check the reading is near zero.

## 8.4 Return to service

- Reinstall and compare with a portable reference meter in the basin.

- Restore automatic control.

# 9. Acceptance criteria

- Air calibration accepted by the analyser within slope limits.

- Zero check near 0 mg/L where performed.

- Process reading within the agreed limit of a portable reference.

# 10. Records

- Calibration master list (free template: instrumentationblog.in/downloads/templates/calibration-master-list/)

- Instrument maintenance log (free template: instrumentationblog.in/downloads/templates/instrument-maintenance-log/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.