| Your Company Name / Logo | DP TRANSMITTER CALIBRATION SOP | Doc no: SOP INST 002 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To calibrate DP transmitters safely and accurately without damaging the sensor through one sided overpressure.

# 2. Scope

DP transmitters with 3 valve or 5 valve manifolds in flow, level and differential pressure service.

# 3. References

- Manufacturer instruction manual

- Instrument data sheet (LRV, URV, square root or linear output)

- Site isolation procedure

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- A DP transmitter can see full line static pressure on one side if the manifold is operated in the wrong order. Always follow the sequence below.

- For steam or hot condensate, allow impulse lines to cool and keep condensate pots filled.

# 6. Tools and equipment

- Low pressure calibrator or hand pump with reference, suitable for the DP range (mbar)

- mA meter or documenting calibrator

- HART communicator

- Vent tubing and container for process fluid

# 7. Prerequisites

- Permit approved; flow or level loop in manual, any trips bypassed under the approved procedure.

- Data sheet values: LRV, URV and whether square root is done in the transmitter or the DCS.

# 8. Procedure

## 8.1 Zero check under static pressure (optional, before isolation)

- Open the equaliser valve with both block valves still open: the transmitter now sees zero DP at line pressure.

- Read the output; a zero shift here (static pressure effect) can be trimmed with a zero trim if the procedure allows.

## 8.2 Removing from service (3 valve manifold)

- Check that the equaliser valve is open.

- Close the high pressure (HP) block valve.

- Close the low pressure (LP) block valve.

- Open the vent valves slowly to release pressure and drain trapped fluid safely.

## 8.3 As found and as left test

- Connect the pressure source to the HP side; leave the LP side vented to atmosphere.

- Close the equaliser valve.

- Apply 0, 25, 50, 75 and 100 % of the DP span upscale and then downscale, recording the mA output.

- If the output is square root, compare against 4 + 16 × √(DP%/100) instead of the linear value.

- Trim the sensor or output if any point is out of tolerance, then record the as left test.

## 8.4 Returning to service (3 valve manifold)

- Close the vent valves and reconnect the impulse lines.

- Check that the equaliser valve is open.

- Open the HP block valve slowly.

- Close the equaliser valve.

- Open the LP block valve slowly.

- Check for leaks and confirm the reading with the control room.

# 9. Acceptance criteria

- As left errors within tolerance at all points.

- Correct manifold valve positions on return: both block valves open, equaliser and vents closed.

- No leaks; DCS reading consistent with the process.

# 10. Records

- Pressure transmitter calibration report (free template: instrumentationblog.in/downloads/templates/pressure-transmitter-calibration-report/)

- HART configuration record (free template: instrumentationblog.in/downloads/templates/hart-transmitter-configuration-record/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.