| Your Company Name / Logo | ESD VALVE PROOF TEST SOP | Doc no: SOP SIS 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To reveal dangerous undetected failures of shutdown valves at the proof test interval assumed in the SIL verification.

# 2. Scope

On/off shutdown valves (ESD, SDV, XV) with solenoid valves and spring return actuators that form part of a SIF.

# 3. References

- IEC 61511 (proof testing of SIS)

- Safety requirements specification (SRS) of the SIF

- Valve and actuator manuals

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Bypassing a SIF reduces protection: apply compensating measures and get written authorisation as per the bypass procedure.

- Only test with the process in a safe state or isolated.

# 6. Tools and equipment

- Stopwatch or SIS sequence of events records

- Communication with the control room (radio)

- Leak test equipment if seat tightness is part of the test

# 7. Prerequisites

- Proof test plan approved; required closing time from the SRS.

- Operations agreement and bypass authorisation where needed.

# 8. Procedure

## 8.1 Preparation

- Review the previous proof test record and any open defects.

- Confirm the required stroke times and fail action from the SRS.

## 8.2 Full stroke test

- Initiate the trip from the SIS logic (through the solenoid valve) as the real demand would.

- Time from the command to the closed limit switch.

- Confirm the closed feedback in the SIS and DCS.

- Reset and open the valve; time the opening stroke and confirm the open feedback.

- Repeat as required by the test plan.

## 8.3 Additional checks

- Check the solenoid valve vents freely and the actuator has no air leaks.

- Perform a seat leak test if the SRS requires tight shut off.

## 8.4 Completion

- Remove all bypasses with operations confirmation.

- Record the results against the SIF and report any failure as a dangerous failure.

# 9. Acceptance criteria

- Closing time within the SRS requirement.

- Feedback correct; smooth travel without sticking.

- Seat leakage within the specified class (where tested).

# 10. Records

- ESD valve stroke test report (free template: instrumentationblog.in/downloads/templates/esd-valve-stroke-test-report/)

- Cause and effect matrix (free template: instrumentationblog.in/downloads/templates/cause-and-effect-matrix-template/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.