| Your Company Name / Logo | EX EQUIPMENT INSPECTION SOP (IEC 60079-17) | Doc no: SOP EX 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To keep equipment in hazardous areas safe by finding defects that could make it an ignition source.

# 2. Scope

Instruments, junction boxes, glands and electrical equipment in Zone 1 and Zone 2 gas areas.

# 3. References

- IEC 60079-17 inspection and maintenance

- IEC 60079-14 design and installation

- Area classification drawings and equipment certificates

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Detailed inspection that opens enclosures needs isolation and a gas free certificate.

- Do not modify certified equipment.

# 6. Tools and equipment

- Inspection checklist

- Torch, mirror and feeler gauges

- Ex equipment register

# 7. Prerequisites

- Area classification and equipment register available.

- Inspector competent in Ex inspection.

# 8. Procedure

## 8.1 Plan

- Select inspection grade: visual, close or detailed, and sample size per the site plan.

## 8.2 General checks

- Equipment suitable for the zone, gas group and temperature class on the drawings.

- Labels legible; no unauthorised modifications.

- Enclosure, glass and seals undamaged; earthing and bonding secure.

## 8.3 Protection specific checks

- Ex d: all bolts present and tight, flame paths clean and undamaged, certified glands and stopping plugs.

- Ex e: terminals tight, no unused openings, correct glands and IP rating.

- Ex i: correct barriers or isolators, IS cables identified and separated, entity documentation current.

## 8.4 Record and act

- Record each item; classify defects by urgency.

- Isolate equipment with serious defects and raise work orders.

# 9. Acceptance criteria

- All equipment inspected per plan with records.

- Serious defects isolated and corrective actions raised.

# 10. Records

- Ex inspection checklist (free template: instrumentationblog.in/downloads/templates/ex-inspection-checklist/)

- Instrument maintenance log (free template: instrumentationblog.in/downloads/templates/instrument-maintenance-log/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.