| Your Company Name / Logo | GUIDED WAVE RADAR LEVEL COMMISSIONING SOP | Doc no: SOP INST 014 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To start GWR transmitters with the right probe, medium and range settings so they measure level and interface reliably.

# 2. Scope

Guided wave radar transmitters with rod, cable or coaxial probes in vessels, chambers and bridles.

# 3. References

- Transmitter manual

- Level data sheet

- Vessel or chamber drawing with nozzle dimensions

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Do not remove probes from pressurised vessels; probes are part of the pressure boundary.

# 6. Tools and equipment

- HART communicator or configuration software with echo curve view

- Tape measure and vessel drawing

# 7. Prerequisites

- Mechanical installation complete; probe length and type match the data sheet.

# 8. Procedure

## 8.1 Installation check

- Probe clear of internals and nozzle walls as the manual requires; centring disc fitted in chambers if needed.

- Probe length, nozzle height and reference point recorded.

## 8.2 Configure

- Enter probe type and length, tank or chamber geometry, reference height and dielectric constant of the product.

- For interface, enter upper layer dielectric and enable interface measurement.

- Set range, damping and failure current.

## 8.3 Echo curve review

- Save the echo curve with the vessel at a known level.

- Identify the level and end of probe peaks; set thresholds or suppress fixed disturbances as the manual allows.

## 8.4 Verify and record

- Compare the reading with a gauge glass or manual dip at two levels if possible.

- Save the configuration backup and record it.

# 9. Acceptance criteria

- Level within the agreed limit of the reference at the checked levels.

- Echo curve clean with a clear level peak.

- Configuration saved and recorded.

# 10. Records

- HART configuration record (free template: instrumentationblog.in/downloads/templates/hart-transmitter-configuration-record/)

- Loop check sheet (free template: instrumentationblog.in/downloads/templates/loop-check-sheet/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.