| Your Company Name / Logo | HART TRANSMITTER CONFIGURATION SOP | Doc no: SOP INST 015 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To configure transmitters correctly the first time and keep a record of every setting.

# 2. Scope

HART pressure, temperature, level and flow transmitters configured in the field or workshop.

# 3. References

- Instrument data sheet

- Manufacturer manual

- Site HART configuration standard

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Use communicators approved for the hazardous area, or work in a safe area.

- Put the loop in manual before changing configuration; changes can move the output.

# 6. Tools and equipment

- HART communicator or modem with software

- Loop power supply and 250 Ω resistor for bench work

- mA meter

# 7. Prerequisites

- Data sheet with the required range, units and alarm direction.

# 8. Procedure

## 8.1 Connect

- Connect the communicator across the transmitter or the loop resistor (at least 250 Ω in the loop).

- Read device identity and present configuration; save it as found.

## 8.2 Configure

- Set tag, descriptor and message.

- Set units, LRV, URV, transfer function and damping per data sheet.

- Set failure direction (upscale or downscale) and NAMUR NE43 levels if selectable.

- Set write protection if required by the site.

## 8.3 Test

- Use the loop test function to drive 4, 12 and 20 mA and confirm the DCS readings.

- Check the process value and units at the DCS.

## 8.4 Record

- Save the as left configuration file and fill the configuration record.

# 9. Acceptance criteria

- Configuration matches the data sheet.

- Loop test values match at the DCS within tolerance.

- As found and as left configurations saved.

# 10. Records

- HART transmitter configuration record (free template: instrumentationblog.in/downloads/templates/hart-transmitter-configuration-record/)

- Instrument maintenance log (free template: instrumentationblog.in/downloads/templates/instrument-maintenance-log/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.