| Your Company Name / Logo | INSTRUMENT LOOP CHECKING SOP (HOT LOOP) | Doc no: SOP COM 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To prove that every instrument loop works correctly from the field device to the control system before start up.

# 2. Scope

Analog and digital inputs and outputs connected to DCS, PLC and SIS during commissioning or after modifications.

# 3. References

- Loop drawings, I/O list and instrument index

- Alarm and trip set point list

- Cold loop and installation check records

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Energised loops: avoid short circuits on terminals; in IS circuits use only certified test equipment.

- Confirm that moving valves or starting motors during the test is safe.

# 6. Tools and equipment

- Loop calibrator (mA source and measure)

- Multimeter

- Radios

- Loop drawings and the loop check sheet

# 7. Prerequisites

- Installation and cold loop checks complete and signed.

- Control system powered and configured; field device configured to the data sheet.

# 8. Procedure

## 8.1 Analog input loops

- Disconnect the transmitter or use loop test mode.

- Inject 4, 8, 12, 16 and 20 mA at the field end.

- Confirm the DCS reading at each point against the expected engineering value.

- Simulate each alarm and trip and confirm it on the HMI and in the event log.

- Simulate below 3.6 mA and above 21 mA (or open circuit) to confirm bad PV alarms.

## 8.2 Analog output loops

- Set the output from the DCS to 0, 25, 50, 75, 100 % and measure the current or the valve position.

## 8.3 Digital loops

- Operate each field contact and confirm the state change in the DCS.

- Force each digital output and confirm the field device responds (solenoid, motor start relay).

## 8.4 Completion

- Reconnect field devices and confirm live process readings.

- Sign the loop check sheet with all parties and raise punch items for faults.

# 9. Acceptance criteria

- Readings within the loop tolerance (typically ± 0.5 % of span).

- Alarms and trips at the correct set points.

- Correct device response for outputs.

# 10. Records

- Loop check sheet (free template: instrumentationblog.in/downloads/templates/loop-check-sheet/)

- Punch list (free template: instrumentationblog.in/downloads/templates/punch-list-template/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.