| Your Company Name / Logo | INSTRUMENT TUBING LEAK TEST SOP | Doc no: SOP COM 003 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To prove that instrument tubing, fittings and valves are leak tight before commissioning.

# 2. Scope

Impulse lines and instrument tubing from the root valve to the instrument manifold.

# 3. References

- Piping and tubing test specification of the project

- Hook up drawings

- Tube fitting manufacturer instructions

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Isolate the instrument from the test: test pressure can exceed its overpressure limit.

- Pneumatic tests store energy: use the lowest pressure allowed by the specification, barricade the area and never stand in front of fittings.

# 6. Tools and equipment

- Hydrostatic test pump or regulated gas supply

- Calibrated test gauge (range about 1.5 to 2 times the test pressure)

- Leak detection fluid (for pneumatic tests)

- Blanking plugs and caps

# 7. Prerequisites

- Tubing complete and supported; fittings made up to the manufacturer gap check.

- Test pressure and hold time taken from the project specification.

# 8. Procedure

## 8.1 Preparation

- Close the manifold block valves or disconnect the instrument and cap the tubing.

- Connect the test pump and test gauge at the highest practical point for venting.

## 8.2 Test

- Fill with water (hydrostatic) and vent air, or pressurise with gas in steps (pneumatic).

- Raise to the specified test pressure and isolate the pump.

- Hold for the specified time (commonly 10 to 30 minutes) and record the start and end pressure.

- Check every joint with leak detection fluid for pneumatic tests, or by inspection for hydrostatic tests.

## 8.3 Completion

- Depressurise slowly, drain water from lines that must be dry, and reconnect the instrument.

- Record the result and raise punch items for any leak.

# 9. Acceptance criteria

- No pressure drop over the hold time (allowing for temperature effects).

- No visible leaks or bubbles at any joint.

# 10. Records

- Instrument installation checklist (free template: instrumentationblog.in/downloads/templates/instrument-installation-checklist/)

- Punch list (free template: instrumentationblog.in/downloads/templates/punch-list-template/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.